{"text_format":"1","workbook":"xlsx","n_sheets":42,"sheets":["INFO","Appendix Cover","W-Priorities","W-Goals","W-Roles","W-TrackingSystem","W-OnSiteDoc","W-WaterConservation","C-OccTurnover","C-Interior_Daily","C-Exterior_Daily","C-Lighting_Daily","C-Meters_Daily","C-Irrigation_Daily","C-Roof_Monthly","C-Roof_Weekly","C-Elevator_Daily","C-CHP_Daily","C-DHW_Annual","C-DHW_Monthly","C-DHW_Daily","C-HWBoiler_Annual","C-HWBoiler_Monthly","C-HWBoiler_Daily","C-SteamBoiler_Annual","C-SteamBoiler_Monthly","C-SteamBoiler_Daily","C-CoolingTower_Annual","C-CoolingTower_Daily","C-Chiller_Daily","C-RTU_Annual","C-RTU_Monthly","C-ForcedAirHeating_Annual","C-ForcedAirHeating_Monthly","C-ForcedAirCooling_Annual","C-ForcedAirCooling_Monthly","C-DuctlessAC_Annual","C-DuctlessAC_Monthly","C-PTAC_Annual","C-PTAC_Monthly","R-SiteFeedback","R-Tools"],"not_rendered":{"charts":0,"images":21,"macros":1,"external_links":0,"defined_names":41,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"INFO","index":0,"n_rows":76,"n_cols":13,"rows_kept":76,"cut":false,"hidden":false,"merged":[[29,5,29,7],[27,5,27,7],[23,5,23,7],[21,5,21,7],[19,5,19,7],[39,5,39,7],[37,5,37,7],[35,5,35,7],[33,5,33,7],[31,5,31,7],[45,1,45,3],[43,1,43,3],[41,1,41,3],[49,5,49,8],[43,5,43,7],[41,5,41,7],[3,0,3,9],[0,0,1,9],[75,0,75,9],[9,1,11,9],[45,5,46,9],[19,1,19,3],[21,1,21,3],[23,1,23,3],[39,1,39,3],[37,1,37,3],[35,1,35,3],[33,1,33,3],[31,1,31,3],[29,1,29,3],[27,1,27,3],[49,1,49,3]]}
["O&M Manual Appendix"]
[]
[]
["The Operations & Maintenance (O&M) Manual Appendix serves as a companion document to the O&M Manual. This Appendix contains supporting documents such as worksheets for creating O&M strategies, checklists to incorporate into preventative maintenance routines, and helpful tips/reference guides. In addition, this serves as a place to include any other supporting documents to the O&M Manual."]
[]
["Step-by-Step Instructions"]
[]
["1. ","When opening the workbook, be sure macros are enabled."]
[]
["2. ","In the 'User Selection' section below, select worksheets, checklists, and reference guides to include in the O&M Manual Appendix. Selections should be made after discussing site needs with operations staff to decide which documents are most appropriate."]
[]
[]
[]
["3. ","Review and print \"Entire Workbook\"."]
[]
["User Selection"]
[]
["Worksheets  (To use a hyperlink, select the checkbox first.)"]
[]
[null,"Setting O&M Priorities",null,null,null,"Establishing a Tracking System",null,null,null,null,null,true,true]
[]
[null,"Setting Property Goals",null,null,null,"Onsite Documentation",null,null,null,null,null,true,true]
[]
[null,"Staff Roles",null,null,null,"Water Conservation",null,null,null,null,null,true,true]
[]
["Preventative Maintenance Checklists*"]
[]
[null,"Occupancy Turnover",null,null,null,"Heating Hot Water Boiler",null,null,null,null,null,true,false]
[]
[null,"Interior",null,null,null,"Heating Steam Boiler",null,null,null,null,null,true,false]
[]
[null,"Exterior",null,null,null,"Cooling Tower",null,null,null,null,null,true,false]
[]
[null,"Lighting",null,null,null,"Chiller",null,null,null,null,null,true,false]
[]
[null,"Meters",null,null,null,"Packaged Rooftop Unit (RTU)",null,null,null,null,null,true,false]
[]
[null,"Irrigation",null,null,null,"Forced Air Heating",null,null,null,null,null,true,false]
[]
[null,"Roof & Exhaust Fans",null,null,null,"Forced Air Cooling",null,null,null,null,null,false,false]
[]
[null,"Elevator",null,null,null,"Ductless AC (Mini Split)",null,null,null,null,null,false,false]
[]
[null,"CHP",null,null,null,"PTAC",null,null,null,null,null,false,false]
[]
[null,"Domestic Hot Water Heater",null,null,"*","Multiple checklists may be included for a system, e.g. annual, monthly, and daily inspections.",null,null,null,null,null,false]
[]
["Tips/Reference"]
[]
[null,"Tips: Respond to Site Feedback",null,null,null,"Reference: Tools for Maintenance Staff",null,null,null,null,null,true,true]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["(Page intentionally left blank)"]

{"sheet":"Appendix Cover","index":1,"n_rows":69,"n_cols":1,"rows_kept":69,"cut":false,"hidden":false,"merged":[[13,0,15,13],[16,0,18,13],[31,0,31,13],[68,0,68,13]]}
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["Operations & Maintenance Manual"]
[]
[]
["Appendix"]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["(Page intentionally left blank)"]

{"sheet":"W-Priorities","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"W-Goals","index":3,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"W-Roles","index":4,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"W-TrackingSystem","index":5,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"W-OnSiteDoc","index":6,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"W-WaterConservation","index":7,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"C-OccTurnover","index":8,"n_rows":27,"n_cols":6,"rows_kept":27,"cut":false,"hidden":false,"merged":[]}
["Interior",null,"BUILDING NAME_______________________________ ",null,"MONTH _________ YEAR__________"]
[null,"APARTMENT INSPECTION","LOCATION ______________________","OPERATOR NAME_______________________________"]
[null,null,"APT # ______________","EMERGENCY CONTACT___________________________"]
[null,"PROCEDURE","DETAILS","COMPLETE?","COMMENTS","SIGN"]
[null,"WATER EFFICIENCY"]
[1,"Confirm efficient showerhead installed in bathrooms.","Maximum flow rate of 1.5 GPM    \n(Check for EPA \"Water Sense\" Rated if packaging available)"]
[2,"Confirm efficient sink aerators installed in bathrooms.","Maximum flow rate of 1.0 GPM \n(Check for EPA \"Water Sense\" Rated if packaging available)"]
[3,"Confirm water efficient toilet installed in bathrooms.","Maximum flow rate of 1.1 GPF \n(Check for EPA \"Water Sense\" Rated if packaging available)"]
[4,"Check all plumbing fixtures for leaks and corrosion."]
[5,"Check toilet tanks for leaks with dye pill.","Replace toilet flapper if leak found."]
[6,"Check hot water temperature.","Call manager if over 120F."]
[null,"ELECTRIC EFFICIENCY"]
[1,"Energy efficient lighting is present.","Confirm that no incandescent or halogen bulbs are present in hard-wired fixtures.  Apartment should only contain CFLs, LEDs, or T8 lighting."]
[2,"Confirm the refrigerator is ENERGY STAR® rated and check refrigerator door seal.","Clean and disconnect (or turn down refrigerator) while unit is vacant."]
[3,"Confirm the dishwasher is ENERGY STAR® rated."]
[4,"Confirm OTHER appliances are ENERGY STAR® rated"]
[null,"HEATING / COOLING EFFICIENCY"]
[1,"Check radiators/ baseboard for leaks, damage and working valves/vents.","Turn off radiator valves while vacant."]
[2,"Ensure heating controls are installed and working.","For baseboard hot water and steam radiators, consider installing Thermostatic Radiator Valves (TRVs).  "]
[3,"Confirm the PTAC unit is ENERGY STAR® rated.","Minimum EER rating of 13.8 (for most common sizes)"]
[4,"Ensure the PTAC/fan-coil unit is cleaned thoroughly.","Follow the procedures on the \"Annual PTAC Task Checklist\""]
[5,"Ensure the cooling controls are set-up properly.","If there is a programmable thermostat, make sure the date and time are set correctly. Leave instructions to show tenant how to program."]
[6,"Record apartment and outdoor temparture."]
[7,"Check all windows/ AC sleeves/ pipe penetrations for air, water, or pest infiltration.  Ensure all windows close and lock tightly. ","Seal any small gaps, report large gaps, windows that don't close and lock."]
[null,"VENTILATION EFFICIENCY"]
[1,"Clean ALL exhaust fan grills.","Exhaust vents located in kitchens and bathrooms.  Grill should be removed and cleaned with a soft detergent."]
[2,"Install constant air regulator (CAR) in ALL exhaust ducts.","The Constant Air Regulator should be selected to meet the maximum ventilation rate of the local code."]

{"sheet":"C-Interior_Daily","index":9,"n_rows":36,"n_cols":16,"rows_kept":36,"cut":false,"hidden":false,"merged":[[33,13,33,14],[33,15,33,16],[34,13,34,14],[34,15,34,16],[35,13,35,14],[35,15,35,16],[30,13,30,14],[30,15,30,16],[31,13,31,14],[31,15,31,16],[32,13,32,14],[32,15,32,16],[27,13,27,14],[27,15,27,16],[28,13,28,14],[28,15,28,16],[29,13,29,14],[29,15,29,16],[24,13,24,14],[24,15,24,16],[25,13,25,14],[25,15,25,16],[26,13,26,14],[26,15,26,16],[21,13,21,14],[21,15,21,16],[22,13,22,14],[22,15,22,16],[23,13,23,14],[23,15,23,16],[18,13,18,14],[18,15,18,16],[19,13,19,14],[19,15,19,16],[20,13,20,14],[20,15,20,16],[15,13,15,14],[15,15,15,16],[16,13,16,14],[16,15,16,16],[17,13,17,14],[17,15,17,16],[12,13,12,14],[12,15,12,16],[13,13,13,14],[13,15,13,16],[14,13,14,14],[14,15,14,16],[9,13,9,14],[9,15,9,16],[10,13,10,14],[10,15,10,16],[11,13,11,14],[11,15,11,16],[6,13,6,14],[6,15,6,16],[7,13,7,14],[7,15,7,16],[8,13,8,14],[8,15,8,16],[5,13,5,14],[5,15,5,16],[3,13,3,14],[3,15,3,16],[4,0,4,2],[4,13,4,14],[4,15,4,16]]}
["INTERIOR",null,null,null,null,null,"BUILDING NAME____________________________________",null,null,null,null,"MONTH________________________",null,null,"YEAR_________"]
[null,"DAILY ENVELOPE INSPECTION",null,null,null,null,null,null,null,null,null,"OPERATOR NAME___________________"]
[null,null,null,null,null,null,null,null,null,null,null,"EMERGENCY CONTACT_______________"]
["DAY","TIME","Outside Air Temp (°F)","Count # doors open","Count # windows open","All doors close and latch fully?","Any doors  slam?","Any gaps or cracks around door or frame?","Any loose hinges or latches?","Weather-stripping and sweep are in good condition on all exterior doors?","All windows close and lock fully?","Signs of air or water around windows, frames or between window sashes?","Any open gaps in walls?","COMMENTS / ISSUES",null,"SIGN"]
["Call Manager IF:",null,null,null,null,"any doors do not close and latch",null,"any gaps or cracks",null,"weather-stip needs replacement",null,"signs of air or water","any open gaps"]
[1]
[2]
[3]
[4]
[5]
[6]
[7]
[8]
[9]
[10]
[11]
[12]
[13]
[14]
[15]
[16]
[17]
[18]
[19]
[20]
[21]
[22]
[23]
[24]
[25]
[26]
[27]
[28]
[29]
[30]
[31]

{"sheet":"C-Exterior_Daily","index":10,"n_rows":35,"n_cols":22,"rows_kept":35,"cut":false,"hidden":false,"merged":[[33,11,33,12],[33,13,33,14],[34,11,34,12],[34,13,34,14],[30,11,30,12],[30,13,30,14],[31,11,31,12],[31,13,31,14],[32,11,32,12],[32,13,32,14],[27,11,27,12],[27,13,27,14],[28,11,28,12],[28,13,28,14],[29,11,29,12],[29,13,29,14],[24,11,24,12],[24,13,24,14],[25,11,25,12],[25,13,25,14],[26,11,26,12],[26,13,26,14],[21,11,21,12],[21,13,21,14],[22,11,22,12],[22,13,22,14],[23,11,23,12],[23,13,23,14],[18,11,18,12],[18,13,18,14],[19,11,19,12],[19,13,19,14],[20,11,20,12],[20,13,20,14],[15,11,15,12],[15,13,15,14],[16,11,16,12],[16,13,16,14],[17,11,17,12],[17,13,17,14],[12,11,12,12],[12,13,12,14],[13,11,13,12],[13,13,13,14],[14,11,14,12],[14,13,14,14],[9,11,9,12],[9,13,9,14],[10,11,10,12],[10,13,10,14],[11,11,11,12],[11,13,11,14],[6,11,6,12],[6,13,6,14],[7,11,7,12],[7,13,7,14],[8,11,8,12],[8,13,8,14],[5,11,5,12],[5,13,5,14],[2,11,2,12],[2,13,2,14],[3,0,3,1],[4,11,4,12],[4,13,4,14]]}
[null,"Exterior",null,null,null,null,null,"BUILDING NAME _____________________________",null,null,null,"MONTH ________________",null,"YEAR ____________",null,"Exterior ","BUILDING NAME____________________________________",null,null,"MONTH________________________",null,"YEAR________"]
[null,"DAILY INSPECTION: General",null,null,null,null,null,"EMERGENCY CONTACT _________________________",null,null,null,"OPERATOR NAME __________________________",null,null,null,{"$f":"B2","v":"DAILY INSPECTION: General"},"Energy Mgmt Contact ____________________________________",null,null,"OPERATOR NAME__________________________"]
["DAY","TIME","Count:\n # lights on in daytime","Count: \n# lights damaged","Dryer vent blocked?","Count: \n# windows open","Signs of damage to building façade? Leaks?","Is rain forecast","Is irrigation ON?","Are non-landscape features getting wet?","Leaks in hose / irrigation connections?","COMMENTS / ISSUES",null,"SIGN",null,"Additional COMMENTS/ISSUES"]
["Call Manager IF:",null,"lights on","lights damaged","can't unblock",null,"façade damaged",null,null,"can't adjust irrigation","can't fix leak"]
[1,null,null,null,"Y       N",null,null,"Y       N","Y       N","Y       N","Y       N"]
[2,null,null,null,"Y       N",null,null,"Y       N","Y       N","Y       N","Y       N"]
[3,null,null,null,"Y       N",null,null,"Y       N","Y       N","Y       N","Y       N"]
[4,null,null,null,"Y       N",null,null,"Y       N","Y       N","Y       N","Y       N"]
[5,null,null,null,"Y       N",null,null,"Y       N","Y       N","Y       N","Y       N"]
[6,null,null,null,"Y       N",null,null,"Y       N","Y       N","Y       N","Y       N"]
[7,null,null,null,"Y       N",null,null,"Y       N","Y       N","Y       N","Y       N"]
[8,null,null,null,"Y       N",null,null,"Y       N","Y       N","Y       N","Y       N"]
[9,null,null,null,"Y       N",null,null,"Y       N","Y       N","Y       N","Y       N"]
[10,null,null,null,"Y       N",null,null,"Y       N","Y       N","Y       N","Y       N"]
[11,null,null,null,"Y       N",null,null,"Y       N","Y       N","Y       N","Y       N"]
[12,null,null,null,"Y       N",null,null,"Y       N","Y       N","Y       N","Y       N"]
[13,null,null,null,"Y       N",null,null,"Y       N","Y       N","Y       N","Y       N"]
[14,null,null,null,"Y       N",null,null,"Y       N","Y       N","Y       N","Y       N"]
[15,null,null,null,"Y       N",null,null,"Y       N","Y       N","Y       N","Y       N"]
[16,null,null,null,"Y       N",null,null,"Y       N","Y       N","Y       N","Y       N"]
[17,null,null,null,"Y       N",null,null,"Y       N","Y       N","Y       N","Y       N"]
[18,null,null,null,"Y       N",null,null,"Y       N","Y       N","Y       N","Y       N"]
[19,null,null,null,"Y       N",null,null,"Y       N","Y       N","Y       N","Y       N"]
[20,null,null,null,"Y       N",null,null,"Y       N","Y       N","Y       N","Y       N"]
[21,null,null,null,"Y       N",null,null,"Y       N","Y       N","Y       N","Y       N"]
[22,null,null,null,"Y       N",null,null,"Y       N","Y       N","Y       N","Y       N"]
[23,null,null,null,"Y       N",null,null,"Y       N","Y       N","Y       N","Y       N"]
[24,null,null,null,"Y       N",null,null,"Y       N","Y       N","Y       N","Y       N"]
[25,null,null,null,"Y       N",null,null,"Y       N","Y       N","Y       N","Y       N"]
[26,null,null,null,"Y       N",null,null,"Y       N","Y       N","Y       N","Y       N"]
[27,null,null,null,"Y       N",null,null,"Y       N","Y       N","Y       N","Y       N"]
[28,null,null,null,"Y       N",null,null,"Y       N","Y       N","Y       N","Y       N"]
[29,null,null,null,"Y       N",null,null,"Y       N","Y       N","Y       N","Y       N"]
[30,null,null,null,"Y       N",null,null,"Y       N","Y       N","Y       N","Y       N"]
[31,null,null,null,"Y       N",null,null,"Y       N","Y       N","Y       N","Y       N"]

{"sheet":"C-Lighting_Daily","index":11,"n_rows":36,"n_cols":13,"rows_kept":36,"cut":false,"hidden":false,"merged":[[35,10,35,11],[35,12,35,13],[32,10,32,11],[32,12,32,13],[33,10,33,11],[33,12,33,13],[34,10,34,11],[34,12,34,13],[29,10,29,11],[29,12,29,13],[30,10,30,11],[30,12,30,13],[31,10,31,11],[31,12,31,13],[26,10,26,11],[26,12,26,13],[27,10,27,11],[27,12,27,13],[28,10,28,11],[28,12,28,13],[23,10,23,11],[23,12,23,13],[24,10,24,11],[24,12,24,13],[25,10,25,11],[25,12,25,13],[20,10,20,11],[20,12,20,13],[21,10,21,11],[21,12,21,13],[22,10,22,11],[22,12,22,13],[17,10,17,11],[17,12,17,13],[18,10,18,11],[18,12,18,13],[19,10,19,11],[19,12,19,13],[14,10,14,11],[14,12,14,13],[15,10,15,11],[15,12,15,13],[16,10,16,11],[16,12,16,13],[11,10,11,11],[11,12,11,13],[12,10,12,11],[12,12,12,13],[13,10,13,11],[13,12,13,13],[8,10,8,11],[8,12,8,13],[9,10,9,11],[9,12,9,13],[10,10,10,11],[10,12,10,13],[5,10,5,11],[5,12,5,13],[6,10,6,11],[6,12,6,13],[7,10,7,11],[7,12,7,13],[3,10,3,11],[3,12,3,13],[4,0,4,1],[4,2,4,5],[4,10,4,11],[4,12,4,13]]}
["Interior",null,null,null,null,"BUILDING________________________________",null,null,null,"MONTH________________________",null,"YEAR________"]
[null,"DAILY LIGHTING",null,null,null,"SPACE NAME & FLOOR_________________________________",null,null,null,"OPERATOR NAME________________________"]
[null,null,null,null,null,null,null,null,null,"EMERGENCY CONTACT___________________"]
["DAY","TIME","Count # lamps burned out","Count # lamps flickering","Count # lenses missing","Count # lenses dirty","Count # lenses damaged","Occ. sensors/bi-level  off/low before entry?","Occ sensors/bi-level on/high after entry?","Manually turn off lights where applicable. (Record locations.)","COMMENTS / ISSUES",null,"SIGN"]
["Call Manager IF:",null,"need assistance to replace",null,null,null,"need assist. to fix","lights not off/low before entry","lights not on/high after entry"]
[1,null,null,null,null,null,null,"Y       N","Y       N"]
[2,null,null,null,null,null,null,"Y       N","Y       N"]
[3,null,null,null,null,null,null,"Y       N","Y       N"]
[4,null,null,null,null,null,null,"Y       N","Y       N"]
[5,null,null,null,null,null,null,"Y       N","Y       N"]
[6,null,null,null,null,null,null,"Y       N","Y       N"]
[7,null,null,null,null,null,null,"Y       N","Y       N"]
[8,null,null,null,null,null,null,"Y       N","Y       N"]
[9,null,null,null,null,null,null,"Y       N","Y       N"]
[10,null,null,null,null,null,null,"Y       N","Y       N"]
[11,null,null,null,null,null,null,"Y       N","Y       N"]
[12,null,null,null,null,null,null,"Y       N","Y       N"]
[13,null,null,null,null,null,null,"Y       N","Y       N"]
[14,null,null,null,null,null,null,"Y       N","Y       N"]
[15,null,null,null,null,null,null,"Y       N","Y       N"]
[16,null,null,null,null,null,null,"Y       N","Y       N"]
[17,null,null,null,null,null,null,"Y       N","Y       N"]
[18,null,null,null,null,null,null,"Y       N","Y       N"]
[19,null,null,null,null,null,null,"Y       N","Y       N"]
[20,null,null,null,null,null,null,"Y       N","Y       N"]
[21,null,null,null,null,null,null,"Y       N","Y       N"]
[22,null,null,null,null,null,null,"Y       N","Y       N"]
[23,null,null,null,null,null,null,"Y       N","Y       N"]
[24,null,null,null,null,null,null,"Y       N","Y       N"]
[25,null,null,null,null,null,null,"Y       N","Y       N"]
[26,null,null,null,null,null,null,"Y       N","Y       N"]
[27,null,null,null,null,null,null,"Y       N","Y       N"]
[28,null,null,null,null,null,null,"Y       N","Y       N"]
[29,null,null,null,null,null,null,"Y       N","Y       N"]
[30,null,null,null,null,null,null,"Y       N","Y       N"]
[31,null,null,null,null,null,null,"Y       N","Y       N"]

{"sheet":"C-Meters_Daily","index":12,"n_rows":36,"n_cols":13,"rows_kept":36,"cut":false,"hidden":false,"merged":[[33,10,33,11],[33,12,33,13],[34,10,34,11],[34,12,34,13],[35,10,35,11],[35,12,35,13],[30,10,30,11],[30,12,30,13],[31,10,31,11],[31,12,31,13],[32,10,32,11],[32,12,32,13],[27,10,27,11],[27,12,27,13],[28,10,28,11],[28,12,28,13],[29,10,29,11],[29,12,29,13],[24,10,24,11],[24,12,24,13],[25,10,25,11],[25,12,25,13],[26,10,26,11],[26,12,26,13],[21,10,21,11],[21,12,21,13],[22,10,22,11],[22,12,22,13],[23,10,23,11],[23,12,23,13],[18,10,18,11],[18,12,18,13],[19,10,19,11],[19,12,19,13],[20,10,20,11],[20,12,20,13],[15,10,15,11],[15,12,15,13],[16,10,16,11],[16,12,16,13],[17,10,17,11],[17,12,17,13],[12,10,12,11],[12,12,12,13],[13,10,13,11],[13,12,13,13],[14,10,14,11],[14,12,14,13],[9,10,9,11],[9,12,9,13],[10,10,10,11],[10,12,10,13],[11,10,11,11],[11,12,11,13],[6,10,6,11],[6,12,6,13],[7,10,7,11],[7,12,7,13],[8,10,8,11],[8,12,8,13],[5,10,5,11],[5,12,5,13],[3,10,3,11],[3,12,3,13],[4,0,4,1],[4,10,4,11],[4,12,4,13]]}
["METERS",null,null,null,null,"BUILDING NAME _____________________________",null,null,null,"MONTH________________________",null,"YEAR_______"]
[null,"DAILY INSPECTION",null,null,null,null,null,null,null,"OPERATOR NAME___________________"]
[null,null,null,null,null,null,null,null,null,"EMERGENCY CONTACT_______________"]
["DAY","TIME","Electric Meter Reading",null,"Gas Meter  Reading",null,"Water Meter Reading",null,"Oil Tank Level","Oil Deliveries","COMMENTS / ISSUES",null,"SIGN"]
["Call Manager IF:",null,"spike noticed",null,"spike noticed",null,"spike noticed",null,"tank low",null,"if comments made"]
[1]
[2]
[3]
[4]
[5]
[6]
[7]
[8]
[9]
[10]
[11]
[12]
[13]
[14]
[15]
[16]
[17]
[18]
[19]
[20]
[21]
[22]
[23]
[24]
[25]
[26]
[27]
[28]
[29]
[30]
[31]

{"sheet":"C-Irrigation_Daily","index":13,"n_rows":37,"n_cols":19,"rows_kept":37,"cut":false,"hidden":false,"merged":[[14,9,14,10],[4,9,4,10],[5,0,5,3],[5,9,5,10],[6,9,6,10],[7,9,7,10],[8,9,8,10],[9,9,9,10],[10,9,10,10],[11,9,11,10],[12,9,12,10],[13,9,13,10],[26,9,26,10],[15,9,15,10],[16,9,16,10],[17,9,17,10],[18,9,18,10],[19,9,19,10],[20,9,20,10],[21,9,21,10],[22,9,22,10],[23,9,23,10],[24,9,24,10],[25,9,25,10],[33,9,33,10],[34,9,34,10],[35,9,35,10],[36,9,36,10],[27,9,27,10],[28,9,28,10],[29,9,29,10],[30,9,30,10],[31,9,31,10],[32,9,32,10]]}
[null,"Water",null,null,null,null,"BUILDING NAME______________________________________",null,null,"MONTH________________________",null,"YEAR________","Water","BUILDING NAME____________________________________",null,null,"MONTH________________________",null,"YEAR________"]
[null,"EXTERIOR WATER DAILY INSPECTION",null,null,null,null,"Energy Mgmt Contact ____________________________________",null,null,"OPERATOR NAME__________________________",null,null,"EXTERIOR WATER DAILY INSPECTION","Energy Mgmt Contact ____________________________________",null,null,"OPERATOR NAME__________________________"]
[null,null,null,null,null,null,null,null,null,"EMERGENCY CONTACT______________________",null,null,null,null,null,null,"EMERGENCY CONTACT______________________"]
[]
["DAY","TIME","Outside Air Temp (°F)","Is rain forecast","Is irrigation ON?","What is the irrigation system schedule? \n(time ON/time OFF)","Are non-landscape features getting wet?","Leaks in hose / irrigation connections?","Dedicated Water Meter Reading (gal.)","COMMENTS/ISSUES\n(additional on pg. 2)",null,"SIGN / INITIAL","Additional COMMENTS/ISSUES"]
["Call Manager IF:",null,null,null,"YES and rain forecast","no schedule programmed","water not hitting plants","leaks found","large change in daily amount","if comments made"]
[1,null,null,"Y       N","Y       N","ON:                          OFF:","  Y       N","Y       N"]
[2,null,null,"Y       N","Y       N","ON:                          OFF:","  Y       N","Y       N"]
[3,null,null,"Y       N","Y       N","ON:                          OFF:","  Y       N","Y       N"]
[4,null,null,"Y       N","Y       N","ON:                          OFF:","  Y       N","Y       N"]
[5,null,null,"Y       N","Y       N","ON:                          OFF:","  Y       N","Y       N"]
[6,null,null,"Y       N","Y       N","ON:                          OFF:","  Y       N","Y       N"]
[7,null,null,"Y       N","Y       N","ON:                          OFF:","  Y       N","Y       N"]
[8,null,null,"Y       N","Y       N","ON:                          OFF:","  Y       N","Y       N"]
[9,null,null,"Y       N","Y       N","ON:                          OFF:","  Y       N","Y       N"]
[10,null,null,"Y       N","Y       N","ON:                          OFF:","  Y       N","Y       N"]
[11,null,null,"Y       N","Y       N","ON:                          OFF:","  Y       N","Y       N"]
[12,null,null,"Y       N","Y       N","ON:                          OFF:","  Y       N","Y       N"]
[13,null,null,"Y       N","Y       N","ON:                          OFF:","  Y       N","Y       N"]
[14,null,null,"Y       N","Y       N","ON:                          OFF:","  Y       N","Y       N"]
[15,null,null,"Y       N","Y       N","ON:                          OFF:","  Y       N","Y       N"]
[16,null,null,"Y       N","Y       N","ON:                          OFF:","  Y       N","Y       N"]
[17,null,null,"Y       N","Y       N","ON:                          OFF:","  Y       N","Y       N"]
[18,null,null,"Y       N","Y       N","ON:                          OFF:","  Y       N","Y       N"]
[19,null,null,"Y       N","Y       N","ON:                          OFF:","  Y       N","Y       N"]
[20,null,null,"Y       N","Y       N","ON:                          OFF:","  Y       N","Y       N"]
[21,null,null,"Y       N","Y       N","ON:                          OFF:","  Y       N","Y       N"]
[22,null,null,"Y       N","Y       N","ON:                          OFF:","  Y       N","Y       N"]
[23,null,null,"Y       N","Y       N","ON:                          OFF:","  Y       N","Y       N"]
[24,null,null,"Y       N","Y       N","ON:                          OFF:","  Y       N","Y       N"]
[25,null,null,"Y       N","Y       N","ON:                          OFF:","  Y       N","Y       N"]
[26,null,null,"Y       N","Y       N","ON:                          OFF:","  Y       N","Y       N"]
[27,null,null,"Y       N","Y       N","ON:                          OFF:","  Y       N","Y       N"]
[28,null,null,"Y       N","Y       N","ON:                          OFF:","  Y       N","Y       N"]
[29,null,null,"Y       N","Y       N","ON:                          OFF:","  Y       N","Y       N"]
[30,null,null,"Y       N","Y       N","ON:                          OFF:","  Y       N","Y       N"]
[31,null,null,"Y       N","Y       N","ON:                          OFF:","  Y       N","Y       N"]

{"sheet":"C-Roof_Monthly","index":14,"n_rows":16,"n_cols":12,"rows_kept":16,"cut":false,"hidden":true,"merged":[[15,1,15,3],[15,4,15,6],[15,8,15,10],[15,11,15,12],[12,1,12,3],[12,4,12,6],[12,8,12,10],[12,11,12,12],[13,1,13,3],[13,4,13,6],[13,8,13,10],[13,11,13,12],[10,1,10,3],[10,4,10,6],[10,8,10,10],[10,11,10,12],[11,1,11,3],[11,4,11,6],[11,8,11,10],[11,11,11,12],[7,1,7,3],[7,4,7,6],[7,8,7,10],[7,11,7,12],[8,1,8,3],[8,4,8,6],[8,8,8,10],[8,11,8,12],[6,1,6,3],[6,4,6,6],[6,8,6,10],[6,11,6,12],[4,1,4,3],[4,4,4,6],[4,8,4,10],[4,11,4,12],[5,11,5,12]]}
["ROOF AND EXHAUST FANS",null,null,null,null,"BUILDING NAME____________________________________",null,null,null,"MONTH________________________",null,"YEAR______"]
[null,"MONTHLY TASKS",null,null,null,"LOCATION ______________",null,null,null,"OPERATOR NAME_____________________"]
[null,null,null,null,null,"EQUIPMENT ID ______________",null,null,null,"EMERGENCY CONTACT_________________"]
[]
[null,"PROCEDURE",null,null,"TASK DETAILS/EXPLANATION",null,null,"COMPLETE?","COMMENTS / ISSUES",null,null,"SIGN"]
[null,"DOORS AND ROOF"]
[1,"Confirm doors/hatches close completely and are air-sealed.",null,null,"If weatherstripping is needed, make note in the comments to the right"]
[2,"Check roof drains for blockages, clean out if needed.",null,null,"Especially during the fall for leaves and during the winter where snow and ice can block drains."]
[3,"Check for debris, standing water, opened roof seams.",null,null,"Check for anything that can lead to damage to the roof surface or potential leaks."]
[null,"MECHANICAL AND LIGHTING"]
[1,"Confirm fans are operating and blowing in the correct direction.",null,null,"Using your hand, confirm exhaust fans are blowing air out of the building.  Turn off the exhaust fan, remove the cover and inspect the condition of the belt, replace if broken, worn, or frayed."]
[2,"Check condition of fan belts, replace if needed.",null,null,"Turn off the exhaust fan, remove the cover and inspect the condition of the belt.  Replace if broken, frayed, or cracked."]
[3,"Check air filters of all AHUs, replace if needed.",null,null,"Open the air filter access door and inspect the condition of the air filters, replace if dirty."]
[4,"Check exterior lighting timers or photocells.",null,null,"Cover the photocell to see if light turns ON and OFF"]
[null,"SOLAR PV AND SOLAR THERMAL"]
[null,"Ensure the surface of the panels are free of debris and dirt.",null,null,"Remove tree branches, bags, or leaves, and spray the surface with a hose or pressure-washer"]

{"sheet":"C-Roof_Weekly","index":15,"n_rows":31,"n_cols":13,"rows_kept":31,"cut":false,"hidden":true,"merged":[[30,10,30,11],[30,12,30,13],[27,10,27,11],[27,12,27,13],[28,10,28,11],[28,12,28,13],[29,10,29,11],[29,12,29,13],[24,10,24,11],[24,12,24,13],[25,10,25,11],[25,12,25,13],[26,10,26,11],[26,12,26,13],[21,10,21,11],[21,12,21,13],[22,10,22,11],[22,12,22,13],[23,10,23,11],[23,12,23,13],[18,10,18,11],[18,12,18,13],[19,10,19,11],[19,12,19,13],[20,10,20,11],[20,12,20,13],[15,10,15,11],[15,12,15,13],[16,10,16,11],[16,12,16,13],[17,10,17,11],[17,12,17,13],[12,10,12,11],[12,12,12,13],[13,10,13,11],[13,12,13,13],[14,10,14,11],[14,12,14,13],[9,10,9,11],[9,12,9,13],[10,10,10,11],[10,12,10,13],[11,10,11,11],[11,12,11,13],[6,10,6,11],[6,12,6,13],[7,10,7,11],[7,12,7,13],[8,10,8,11],[8,12,8,13],[5,10,5,11],[5,12,5,13],[3,10,3,11],[3,12,3,13],[4,0,4,2],[4,10,4,11],[4,12,4,13]]}
["ROOF AND EXHAUST FANS",null,null,null,null,null,"BUILDING NAME _________________________",null,null,null,"MONTH________________________",null,"YEAR____"]
[null,"WEEKLY INSPECTION",null,null,null,null,"QUESTIONS? CONTACT Energy Manager _______________________",null,null,null,"OPERATOR NAME_____________________"]
[null,null,null,null,null,null,null,null,null,null,"EMERGENCY CONTACT________________"]
["WEEK","DATE","TIME","Roof Lighting OFF during DAY?","Roof Doors/Hatch Closed Tightly?","Signs of Standing Water?","Blocked Roof Drains?","All Exhaust Fans Functional?","All AHUs Functional?","Record total kW-hr of\n Solar PV \n(if applicable)","COMMENTS / ISSUES",null,"SIGN"]
["Call Manager IF:",null,null,"Lighting ON","Not closed","standing water present","drains blocked","fans not functional","AHUs not functional","no change in kWh","if comments made"]
[1,null,null,"ON    OFF","Y       N","Y       N","Y       N","Y       N","Y       N"]
[2,null,null,"ON    OFF","Y       N","Y       N","Y       N","Y       N","Y       N"]
[3,null,null,"ON    OFF","Y       N","Y       N","Y       N","Y       N","Y       N"]
[4,null,null,"ON    OFF","Y       N","Y       N","Y       N","Y       N","Y       N"]
[5,null,null,"ON    OFF","Y       N","Y       N","Y       N","Y       N","Y       N"]
[6,null,null,"ON    OFF","Y       N","Y       N","Y       N","Y       N","Y       N"]
[7,null,null,"ON    OFF","Y       N","Y       N","Y       N","Y       N","Y       N"]
[8,null,null,"ON    OFF","Y       N","Y       N","Y       N","Y       N","Y       N"]
[9,null,null,"ON    OFF","Y       N","Y       N","Y       N","Y       N","Y       N"]
[10,null,null,"ON    OFF","Y       N","Y       N","Y       N","Y       N","Y       N"]
[11,null,null,"ON    OFF","Y       N","Y       N","Y       N","Y       N","Y       N"]
[12,null,null,"ON    OFF","Y       N","Y       N","Y       N","Y       N","Y       N"]
[13,null,null,"ON    OFF","Y       N","Y       N","Y       N","Y       N","Y       N"]
[14,null,null,"ON    OFF","Y       N","Y       N","Y       N","Y       N","Y       N"]
[15,null,null,"ON    OFF","Y       N","Y       N","Y       N","Y       N","Y       N"]
[16,null,null,"ON    OFF","Y       N","Y       N","Y       N","Y       N","Y       N"]
[17,null,null,"ON    OFF","Y       N","Y       N","Y       N","Y       N","Y       N"]
[18,null,null,"ON    OFF","Y       N","Y       N","Y       N","Y       N","Y       N"]
[19,null,null,"ON    OFF","Y       N","Y       N","Y       N","Y       N","Y       N"]
[20,null,null,"ON    OFF","Y       N","Y       N","Y       N","Y       N","Y       N"]
[21,null,null,"ON    OFF","Y       N","Y       N","Y       N","Y       N","Y       N"]
[22,null,null,"ON    OFF","Y       N","Y       N","Y       N","Y       N","Y       N"]
[23,null,null,"ON    OFF","Y       N","Y       N","Y       N","Y       N","Y       N"]
[24,null,null,"ON    OFF","Y       N","Y       N","Y       N","Y       N","Y       N"]
[25,null,null,"ON    OFF","Y       N","Y       N","Y       N","Y       N","Y       N"]
[26,null,null,"ON    OFF","Y       N","Y       N","Y       N","Y       N","Y       N"]

{"sheet":"C-Elevator_Daily","index":16,"n_rows":36,"n_cols":14,"rows_kept":36,"cut":false,"hidden":true,"merged":[[33,11,33,12],[33,13,33,14],[34,11,34,12],[34,13,34,14],[35,11,35,12],[35,13,35,14],[30,11,30,12],[30,13,30,14],[31,11,31,12],[31,13,31,14],[32,11,32,12],[32,13,32,14],[27,11,27,12],[27,13,27,14],[28,11,28,12],[28,13,28,14],[29,11,29,12],[29,13,29,14],[24,11,24,12],[24,13,24,14],[25,11,25,12],[25,13,25,14],[26,11,26,12],[26,13,26,14],[21,11,21,12],[21,13,21,14],[22,11,22,12],[22,13,22,14],[23,11,23,12],[23,13,23,14],[18,11,18,12],[18,13,18,14],[19,11,19,12],[19,13,19,14],[20,11,20,12],[20,13,20,14],[15,11,15,12],[15,13,15,14],[16,11,16,12],[16,13,16,14],[17,11,17,12],[17,13,17,14],[12,11,12,12],[12,13,12,14],[13,11,13,12],[13,13,13,14],[14,11,14,12],[14,13,14,14],[9,11,9,12],[9,13,9,14],[10,11,10,12],[10,13,10,14],[11,11,11,12],[11,13,11,14],[6,11,6,12],[6,13,6,14],[7,11,7,12],[7,13,7,14],[8,11,8,12],[8,13,8,14],[5,11,5,12],[5,13,5,14],[3,11,3,12],[3,13,3,14],[4,0,4,2],[4,11,4,12],[4,13,4,14]]}
["ELEVATOR",null,null,null,null,null,null,"BUILDING NAME____________________________________",null,null,"MONTH________________________",null,"YEAR________"]
[null,"DAILY ELEVATOR ROOM INSPECTION",null,null,null,null,null,"Energy Mgmt Contact ____________________________________",null,null,"OPERATOR NAME___________________"]
[null,null,null,null,null,null,null,null,null,null,"EMERGENCY CONTACT_______________"]
["DAY","TIME","Outside Air Temp (°F)","Is door self-closing and locked?","Room Air Temp (Deg F)","Is the A/C system working?","What is the A/C temp set point (°F)?","Are the A/C air filters clean?","Is room free of clutter / unauthorized storage?","Is elevator shaft vent clear and uobstructed?","Is the elevator maintenance logbook present?","COMMENTS",null,"SIGN"]
["Call Manager IF:",null,null,"Not true","above 85°","not operational","below 80°","not clean","clutter present","obstruction present","logbook missing OR no entries","if comments made"]
[1]
[2]
[3]
[4]
[5]
[6]
[7]
[8]
[9]
[10]
[11]
[12]
[13]
[14]
[15]
[16]
[17]
[18]
[19]
[20]
[21]
[22]
[23]
[24]
[25]
[26]
[27]
[28]
[29]
[30]
[31]

{"sheet":"C-CHP_Daily","index":17,"n_rows":36,"n_cols":16,"rows_kept":36,"cut":false,"hidden":true,"merged":[[3,13,3,14],[3,15,3,16],[4,0,4,2],[4,3,4,4],[4,6,4,7],[4,8,4,11],[4,13,4,14],[4,15,4,16],[5,13,5,14],[5,15,5,16],[6,13,6,14],[6,15,6,16],[7,13,7,14],[7,15,7,16],[8,13,8,14],[8,15,8,16],[9,13,9,14],[9,15,9,16],[10,13,10,14],[10,15,10,16],[11,13,11,14],[11,15,11,16],[12,13,12,14],[12,15,12,16],[13,13,13,14],[13,15,13,16],[14,13,14,14],[14,15,14,16],[15,13,15,14],[15,15,15,16],[16,13,16,14],[16,15,16,16],[17,13,17,14],[17,15,17,16],[18,13,18,14],[18,15,18,16],[19,13,19,14],[19,15,19,16],[20,13,20,14],[20,15,20,16],[21,13,21,14],[21,15,21,16],[22,13,22,14],[22,15,22,16],[23,13,23,14],[23,15,23,16],[24,13,24,14],[24,15,24,16],[25,13,25,14],[25,15,25,16],[26,13,26,14],[26,15,26,16],[27,13,27,14],[27,15,27,16],[28,13,28,14],[28,15,28,16],[29,13,29,14],[29,15,29,16],[30,13,30,14],[30,15,30,16],[31,13,31,14],[31,15,31,16],[35,13,35,14],[35,15,35,16],[32,13,32,14],[32,15,32,16],[33,13,33,14],[33,15,33,16],[34,13,34,14],[34,15,34,16]]}
["COMBINED HEAT AND POWER",null,null,null,null,null,null,null,null,null,null,null,"MONTH________________________",null,"YEAR____________"]
[null,"DAILY INSPECTION",null,null,null,null,"BUILDING NAME _________________________",null,null,null,null,null,"OPERATOR NAME___________________"]
[null,null,null,null,null,null,null,null,null,null,null,null,"EMERGENCY CONTACT_______________"]
["DAY","TIME","Outside Air Temp (°F)","Equipment Status (ON/OFF)"," Runtime (hours)","Electric Power (kW)","Phase A Current","Generator Speed (RPM)","Water Inlet Temp (°F)","Water Outlet Temp (°F)","Coolant Temp (°F)","Coolant Press (psi)","Gas Meter Reading","COMMENTS / ISSUES",null,"SIGN / INITIAL"]
["Call Manager IF:",null,null,"not operational",null,"below maximum","abnormal range",null,"depends on system",null,null,null,"not working","if comments made"]
[1]
[2]
[3]
[4]
[5]
[6]
[7]
[8]
[9]
[10]
[11]
[12]
[13]
[14]
[15]
[16]
[17]
[18]
[19]
[20]
[21]
[22]
[23]
[24]
[25]
[26]
[27]
[28]
[29]
[30]
[31]

{"sheet":"C-DHW_Annual","index":18,"n_rows":11,"n_cols":12,"rows_kept":11,"cut":false,"hidden":true,"merged":[[5,1,5,3],[5,4,5,6],[5,8,5,10],[5,11,5,12],[3,1,3,3],[3,4,3,6],[3,8,3,10],[3,11,3,12],[4,11,4,12],[6,1,6,3],[6,4,6,6],[6,8,6,10],[6,11,6,12],[7,1,7,3],[7,4,7,6],[7,8,7,10],[7,11,7,12],[8,1,8,3],[8,4,8,6],[8,8,8,10],[8,11,8,12],[9,1,9,3],[9,4,9,6],[9,8,9,10],[9,11,9,12],[10,1,10,3],[10,4,10,6],[10,8,10,10],[10,11,10,12],[11,1,11,3],[11,4,11,6],[11,8,11,10],[11,11,11,12]]}
["DOMESTIC HOT WATER HEATER",null,null,null,null,null,"BUILDING NAME____________________________________",null,null,"MONTH________________________",null,"YEAR_________"]
[null,"ANNUAL TASKS",null,null,null,null,"LOCATION ______________________________",null,null,"OPERATOR NAME_____________________"]
[null,null,null,null,null,null,"EQUIPMENT ID __________________________",null,null,"EMERGENCY CONTACT_________________"]
[null,"PROCEDURE",null,null,"TASK DETAILS/EXPLANATION",null,null,"COMPLETE?","COMMENTS / ISSUES",null,null,"SIGN"]
[]
[1,"Remove tank sediment",null,null,"Drain the tank by closing the cold water supply valve and opening the bottom blow-down valve."]
[2,"Remove lime scale build-up",null,null,"Lime scale reduces heating efficiency as it accumulates inside a water heater. Heating transfer surfaces become coated with lime scale deposits which increases fuel costs to operate the water heater. To dissolve and remove more stubborn lime scale deposits, a delimer should be used."]
[3,"Inspect anode rods",null,null,"Close the cold water supply line valve, open a near-by faucet and drain some of the hot water from the tank to relieve some pressure.  Remove the anode rod to inspect if it is still working, clean the rod with a soft cloth and reinstall."]
[4,"Test the pressure relief valve",null,null,"Pull the manual lever on the relief valve.  The valve should re-seat unless there is sediment blocking it.  If it does not re-seat, it must be replaced."]
[5,"Clean burner (Gas Only)",null,null,"Using a wire brush and vacuum, clean out the surfaces of the burner, including the main burner assembly (or blower-wheel in forced burners)."]
[6,"Inspect and clean exhaust flue (Gas Only)",null,null,"Inspect the flue for blockages and soot, remove soot with a wire brush and vacuum."]

{"sheet":"C-DHW_Monthly","index":19,"n_rows":8,"n_cols":12,"rows_kept":8,"cut":false,"hidden":true,"merged":[[5,1,5,3],[5,4,5,6],[5,8,5,10],[5,11,5,12],[3,1,3,3],[3,4,3,6],[3,8,3,10],[3,11,3,12],[4,11,4,12],[6,1,6,3],[6,4,6,6],[6,8,6,10],[6,11,6,12],[7,1,7,3],[7,4,7,6],[7,8,7,10],[7,11,7,12]]}
["DOMESTIC HOT WATER HEATER",null,null,null,null,"BUILDING NAME__________________________",null,null,null,"MONTH________________________",null,"YEAR______"]
[null,"MONTHLY TASKS",null,null,null,"LOCATION _________________________________",null,null,null,"OPERATOR NAME_____________________"]
[null,null,null,null,null,"EQUIPMENT ID ______________________________",null,null,null,"EMERGENCY CONTACT_________________"]
[null,"PROCEDURE",null,null,"TASK DETAILS/EXPLANATION",null,null,"COMPLETE?","COMMENTS / ISSUES",null,null,"SIGN"]
[]
[1,"Remove tank sediment",null,null,"Drain the tank by closing the cold water supply valve and opening the bottom blow-down valve."]
[2,"Remove lime scale build-up",null,null,"Lime scale reduces heating efficiency as it accumulates inside a water heater. Heating transfer surfaces become coated with lime scale deposits which increases fuel costs to operate the water heater. To dissolve and remove more stubborn lime scale deposits, a delimer should be used."]
[3,"Confirm proper aquastat set point temperature",null,null,"Temperature should be set to the lowest setting to enable 120 deg F at the apartment sinks."]

{"sheet":"C-DHW_Daily","index":20,"n_rows":36,"n_cols":19,"rows_kept":36,"cut":false,"hidden":true,"merged":[[5,8,5,9],[5,10,5,11],[3,8,3,9],[3,10,3,11],[4,0,4,1],[4,8,4,9],[4,10,4,11],[6,8,6,9],[6,10,6,11],[7,8,7,9],[7,10,7,11],[8,8,8,9],[8,10,8,11],[9,8,9,9],[9,10,9,11],[10,8,10,9],[10,10,10,11],[11,8,11,9],[11,10,11,11],[12,8,12,9],[12,10,12,11],[13,8,13,9],[13,10,13,11],[14,8,14,9],[14,10,14,11],[15,8,15,9],[15,10,15,11],[16,8,16,9],[16,10,16,11],[17,8,17,9],[17,10,17,11],[18,8,18,9],[18,10,18,11],[19,8,19,9],[19,10,19,11],[20,8,20,9],[20,10,20,11],[21,8,21,9],[21,10,21,11],[22,8,22,9],[22,10,22,11],[23,8,23,9],[23,10,23,11],[24,8,24,9],[24,10,24,11],[25,8,25,9],[25,10,25,11],[26,8,26,9],[26,10,26,11],[27,8,27,9],[27,10,27,11],[28,8,28,9],[28,10,28,11],[29,8,29,9],[29,10,29,11],[30,8,30,9],[30,10,30,11],[31,8,31,9],[31,10,31,11],[32,8,32,9],[32,10,32,11],[33,8,33,9],[33,10,33,11],[34,8,34,9],[34,10,34,11],[35,8,35,9],[35,10,35,11]]}
[null,"DOMESTIC HOT WATER",null,null,null,null,"BUILDING NAME____________________________________",null,null,"MONTH________________________",null,"YEAR_____","DOMESTIC HOT WATER","BUILDING NAME____________________________________",null,null,"MONTH________________________",null,"YEAR________"]
[null,"DAILY DHW INSPECTION",null,null,null,null,"Energy Mgmt Contact ____________________________________",null,null,"OPERATOR NAME_______________________________",null,null,{"$f":"B2","v":"DAILY DHW INSPECTION"},"Energy Mgmt Contact ____________________________________",null,null,"OPERATOR NAME__________________________"]
[null,null,null,null,null,null,null,null,null,"EMERGENCY CONTACT________________________",null,null,null,null,null,null,"EMERGENCY CONTACT______________________"]
["DAY","TIME","Hot Water Temperature Setting  (°F)","Hot Water Supply Temp (°F)","Hot Water Return Temp (if applicable) (°F)","Check Pumps for Operation / Leaks","Dedicated Water Meter Reading (gal.)","Dedicated Gas Meter Reading","COMMENTS / ISSUES",null,"SIGN",null,"Additional COMMENTS/ISSUES"]
["Call Manager IF:",null,"above 130°F","above 130°F","depends on system","leaks present","change in daily amount","change in daily amount","if comments made"]
[1]
[2]
[3]
[4]
[5]
[6]
[7]
[8]
[9]
[10]
[11]
[12]
[13]
[14]
[15]
[16]
[17]
[18]
[19]
[20]
[21]
[22]
[23]
[24]
[25]
[26]
[27]
[28]
[29]
[30]
[31]

{"sheet":"C-HWBoiler_Annual","index":21,"n_rows":24,"n_cols":12,"rows_kept":24,"cut":false,"hidden":true,"merged":[[5,1,5,3],[5,4,5,6],[5,8,5,10],[5,11,5,12],[3,1,3,3],[3,4,3,6],[3,8,3,10],[3,11,3,12],[4,11,4,12],[6,1,6,3],[6,4,6,6],[6,8,6,10],[6,11,6,12],[7,1,7,3],[7,4,7,6],[7,8,7,10],[7,11,7,12],[8,1,8,3],[8,4,8,6],[8,8,8,10],[8,11,8,12],[10,1,10,3],[10,4,10,6],[10,8,10,10],[10,11,10,12],[11,1,11,3],[11,4,11,6],[11,8,11,10],[11,11,11,12],[12,1,12,3],[12,4,12,6],[12,8,12,10],[12,11,12,12],[13,1,13,3],[13,4,13,6],[13,8,13,10],[13,11,13,12],[14,1,14,3],[14,4,14,6],[14,8,14,10],[14,11,14,12],[15,1,15,3],[15,4,15,6],[15,8,15,10],[15,11,15,12],[19,1,19,3],[19,4,19,6],[19,8,19,10],[19,11,19,12],[23,1,23,3],[23,4,23,6],[23,8,23,10],[23,11,23,12],[20,11,20,12],[21,1,21,3],[21,4,21,6],[21,8,21,10],[21,11,21,12],[22,1,22,3],[22,4,22,6],[22,8,22,10],[22,11,22,12]]}
["Hot Water Boiler (PAGE 1)",null,null,null,null,null,"BUILDING NAME____________________________________",null,null,"MONTH________________________",null,"YEAR______"]
[null,"ANNUAL TASKS/SUMMER OVERHAUL",null,null,null,null,"LOCATION _______________________________",null,null,"OPERATOR NAME_______________________"]
[null,"*This task may require special service training",null,null,null,null,"EQUIPMENT ID ____________________________",null,null,"EMERGENCY CONTACT___________________"]
["#","PROCEDURE",null,null,"TASK DETAILS/EXPLANATION",null,null,"COMPLETE?","COMMENTS / ISSUES",null,null,"SIGN"]
[null,"SAFETY AND EFFICIENCY TESTS"]
[1,"Test low-water cut-offs",null,null,"Ensure that the low water cutoff device(s) function(s) properly. Test in accordance with the manufacturer’s instructions included with the device(s)."]
[2,"Test the pressure relief valves",null,null,"The relief valve should vent water when the test lever is lifted. It should not weep or discharge water at normal system pressure."]
[3,"Clean and adjust burner components*",null,null,"Inspect burner components; diffuser, nozzle, IR/UV scanner, electrode, etc.  Clean if dirty.  Replace if broken.  "]
[4,"Conduct a boiler efficiency test*",null,null,"Use a combustion analyzer to ensure that the burner is adjusted properly.  Attach the printout to this form or write the results in the comment box to the right.  This must be done any time a change is made which affects the fuel or air ratio entering the burner."]
[null,"CLEANING/TUNING"]
[1,"Clean the fireside of the boiler (Oil Only)*",null,null,"If the flue temperature exceeds 550°F, clean the boiler."]
[2,"Clean waterside of the boiler*",null,null,"Drain the boiler and inspect the waterside through access ports.  Use a droplight to inspect for scale build-up.  Use a pressure washer to remove scale.  Thoroughly flush out through the blow-downs or bottom ports."]
[3,"Clean the exhaust flue",null,null,"Thoroughly inspect the exhaust flue for any signs of\nblockage, corrosion or leakage."]
[4,"Blowdown the air separator",null,null,"Blow-down the air separator to remove sediment.  Only blow-down long enough to see clear water."]
[5,"Confirm correct air pressure in the expansion tank*",null,null,"The expansion tank should have approximately 10psi for every 20 feet of building height (to the highest radiator).  Confirm the correct air pressure by observing the gauge on the tank or using a portable gauge.  Record the pressure in the comment box."]
[6,"Confirm proper flame*",null,null,"Observe the flame during combustion, ensure it has the correct color and shape and is not making contact with the refractory walls of the boiler."]
["Hot Water Boiler (PAGE 2)",null,null,null,null,null,"BUILDING NAME____________________________________",null,null,"MONTH________________________",null,"YEAR______"]
[null,"ANNUAL TASKS/SUMMER OVERHAUL",null,null,null,null,"LOCATION _______________________________",null,null,"OPERATOR NAME_______________________"]
[null,"*This task may require special service training",null,null,null,null,"EQUIPMENT ID ____________________________",null,null,"EMERGENCY CONTACT___________________"]
["#","PROCEDURE",null,null,"TASK DETAILS/EXPLANATION",null,null,"COMPLETE?","COMMENTS / ISSUES",null,null,"SIGN"]
[null,"CLEANING/ TUNING (Continued)"]
[7,"Ensure proper Aquastat settings",null,null,"Observe the boiler through at least one complete cycle.  Make note of what water temperature the boiler turns ON and what temperature the boiler turns OFF.  Write the time of the cycle in the comment box to the right."]
[8,"Ensure efficiency controls are working properly",null,null,"Observe the boiler through at least one complete cycle.  Make note of the  outside temperature and how long the cycle lasts.  Record how long between two boiler cycles."]
[9,"Clean oil filters (Oil Only)",null,null,"If burning oil, clean or replace the fuel oil filters."]

{"sheet":"C-HWBoiler_Monthly","index":22,"n_rows":16,"n_cols":12,"rows_kept":16,"cut":false,"hidden":true,"merged":[[5,1,5,3],[5,4,5,6],[5,8,5,10],[5,11,5,12],[3,1,3,3],[3,4,3,6],[3,8,3,10],[3,11,3,12],[4,11,4,12],[6,1,6,3],[6,4,6,6],[6,8,6,10],[6,11,6,12],[7,1,7,3],[7,4,7,6],[7,8,7,10],[7,11,7,12],[9,1,9,3],[9,4,9,6],[9,8,9,10],[9,11,9,12],[10,1,10,3],[10,4,10,6],[10,8,10,10],[10,11,10,12],[11,1,11,3],[11,4,11,6],[11,8,11,10],[11,11,11,12],[12,1,12,3],[12,4,12,6],[12,8,12,10],[12,11,12,12],[15,1,15,3],[15,4,15,6],[15,8,15,10],[15,11,15,12],[13,1,13,3],[13,4,13,6],[13,8,13,10],[13,11,13,12],[14,1,14,3],[14,4,14,6],[14,8,14,10],[14,11,14,12]]}
["Hot Water Boiler ",null,null,null,null,null,"BUILDING NAME____________________________________",null,null,"MONTH________________________",null,"YEAR______"]
[null,"MONTHLY TASKS",null,null,null,null,"LOCATION _______________________________",null,null,"OPERATOR NAME_______________________"]
[null,null,null,null,null,null,"EQUIPMENT ID ____________________________",null,null,"EMERGENCY CONTACT___________________"]
["#","PROCEDURE",null,null,"TASK DETAILS/EXPLANATION",null,null,"COMPLETE?","COMMENTS / ISSUES",null,null,"SIGN"]
[null,"SAFETY AND EFFICIENCY TESTS"]
[1,"Test low-water cut-offs",null,null,"Ensure that the low water cutoff device(s) function(s) properly. Test in accordance with the manufacturer’s instructions included with the device(s)."]
[2,"Test the pressure relief valves",null,null,"The relief valve should vent water when the test lever is lifted. It should not weep or discharge water at normal system pressure."]
[3,"Conduct a boiler efficiency test*",null,null,"Use a combustion analyzer to ensure that the burner is adjusted properly.  Attach the printout to this form or write the results in the comment box to the right.  This must be done any time a change is made which affects the fuel or air ratio entering the burner."]
[null,"CLEANING/TUNING"]
[1,"Clean the fireside of the boiler (Oil Only)*",null,null,"If the flue temperature exceeds 550°F, clean the boiler."]
[2,"Clean the exhaust flue",null,null,"Thoroughly inspect the exhaust flue for any signs of blockage, corrosion or leakage."]
[3,"Blowdown the air separator",null,null,"Blow-down the air separator to remove sediment.  Only blow-down long enough to see clear water."]
[5,"Confirm proper flame*",null,null,"Observe the flame during combustion, ensure it has the correct color and shape and is not making contact with the refractory walls of the boiler."]
[6,"Ensure proper aqua stat settings*",null,null,"Observe the boiler through at least one complete cycle.  Make note of what water temperature the boiler turns ON and what temperature the boiler turns OFF.  Write the time of the cycle in the comment box to the right."]
[7,"Ensure efficiency controls are working properly",null,null,"Observe the boiler through at least one complete cycle.  Make note of the the outside temperature and how long the cycle lasts.  Record how long between two boiler cycles."]
[8,"Clean oil filters (Oil Only)",null,null,"If burning oil, clean or replace the fuel oil filters."]

{"sheet":"C-HWBoiler_Daily","index":23,"n_rows":36,"n_cols":23,"rows_kept":36,"cut":false,"hidden":true,"merged":[[5,12,5,13],[5,14,5,15],[3,12,3,13],[3,14,3,15],[4,0,4,2],[4,12,4,13],[4,14,4,15],[6,12,6,13],[6,14,6,15],[7,12,7,13],[7,14,7,15],[8,12,8,13],[8,14,8,15],[9,12,9,13],[9,14,9,15],[10,12,10,13],[10,14,10,15],[11,12,11,13],[11,14,11,15],[12,12,12,13],[12,14,12,15],[13,12,13,13],[13,14,13,15],[14,12,14,13],[14,14,14,15],[15,12,15,13],[15,14,15,15],[16,12,16,13],[16,14,16,15],[17,12,17,13],[17,14,17,15],[18,12,18,13],[18,14,18,15],[19,12,19,13],[19,14,19,15],[20,12,20,13],[20,14,20,15],[21,12,21,13],[21,14,21,15],[22,12,22,13],[22,14,22,15],[23,12,23,13],[23,14,23,15],[24,12,24,13],[24,14,24,15],[25,12,25,13],[25,14,25,15],[26,12,26,13],[26,14,26,15],[27,12,27,13],[27,14,27,15],[28,12,28,13],[28,14,28,15],[29,12,29,13],[29,14,29,15],[30,12,30,13],[30,14,30,15],[31,12,31,13],[31,14,31,15],[32,12,32,13],[32,14,32,15],[33,12,33,13],[33,14,33,15],[34,12,34,13],[34,14,34,15],[35,12,35,13],[35,14,35,15]]}
[null,"HOT WATER BOILER",null,null,null,null,"BUILDING____________________________________",null,null,null,null,"MONTH________________________",null,null,"YEAR_________",null,"HOT WATER BOILER",null,"BUILDING____________________________________",null,"MONTH________________________",null,"YEAR_____"]
[null,"DAILY INSPECTION",null,null,null,null,"LOCATION _______________________________",null,null,null,null,"OPERATOR NAME___________________",null,null,null,null,{"$f":"B2","v":"DAILY INSPECTION"},null,"LOCATION _______________________________",null,"OPERATOR NAME___________________"]
[null,null,null,null,null,null,"EQUIPMENT ID ____________________________",null,null,null,null,"EMERGENCY CONTACT_______________",null,null,null,null,null,null,"EQUIPMENT ID ____________________________",null,"EMERGENCY CONTACT_______________"]
["DAY","TIME","Outside Air Temp (°F)","Burner Control Set on AUTO?","Burner Runtime (hours)","Highest Stack Temp (°F)","Operating Aquastat Setting (°F)","Hot Water Supply Temp (°F)","Hot Water Return Temp (°F)","Check Pumps for Leaks","Make-up Water Reading (gal.)","Gas Meter Reading","COMMENTS / ISSUES",null,"SIGN",null,"Additional COMMENTS/ISSUES"]
["Call Manager IF:",null,null,"NO","spike noticed","above 500","above 180","above 180","below 140","leaks present","spike noticed","spike noticed","if comments made"]
[1,null,null,"Y       N"]
[2,null,null,"Y       N"]
[3,null,null,"Y       N"]
[4,null,null,"Y       N"]
[5,null,null,"Y       N"]
[6,null,null,"Y       N"]
[7,null,null,"Y       N"]
[8,null,null,"Y       N"]
[9,null,null,"Y       N"]
[10,null,null,"Y       N"]
[11,null,null,"Y       N"]
[12,null,null,"Y       N"]
[13,null,null,"Y       N"]
[14,null,null,"Y       N"]
[15,null,null,"Y       N"]
[16,null,null,"Y       N"]
[17,null,null,"Y       N"]
[18,null,null,"Y       N"]
[19,null,null,"Y       N"]
[20,null,null,"Y       N"]
[21,null,null,"Y       N"]
[22,null,null,"Y       N"]
[23,null,null,"Y       N"]
[24,null,null,"Y       N"]
[25,null,null,"Y       N"]
[26,null,null,"Y       N"]
[27,null,null,"Y       N"]
[28,null,null,"Y       N"]
[29,null,null,"Y       N"]
[30,null,null,"Y       N"]
[31,null,null,"Y       N"]

{"sheet":"C-SteamBoiler_Annual","index":24,"n_rows":24,"n_cols":12,"rows_kept":24,"cut":false,"hidden":true,"merged":[[3,1,3,3],[3,4,3,6],[3,8,3,10],[3,11,3,12],[4,11,4,12],[8,1,8,3],[8,4,8,6],[8,8,8,10],[8,11,8,12],[5,1,5,3],[5,4,5,6],[5,8,5,10],[5,11,5,12],[6,1,6,3],[6,4,6,6],[6,8,6,10],[6,11,6,12],[7,1,7,3],[7,4,7,6],[7,8,7,10],[7,11,7,12],[9,11,9,12],[11,1,11,3],[11,4,11,6],[11,8,11,10],[11,11,11,12],[10,1,10,3],[10,4,10,6],[10,8,10,10],[10,11,10,12],[12,1,12,3],[12,4,12,6],[12,8,12,10],[12,11,12,12],[13,1,13,3],[13,4,13,6],[13,8,13,10],[13,11,13,12],[14,1,14,3],[14,4,14,6],[14,8,14,10],[14,11,14,12],[15,1,15,3],[15,4,15,6],[15,8,15,10],[15,11,15,12],[19,1,19,3],[19,4,19,6],[19,8,19,10],[19,11,19,12],[23,1,23,3],[23,4,23,6],[23,8,23,10],[23,11,23,12],[21,1,21,3],[21,4,21,6],[21,8,21,10],[21,11,21,12],[22,1,22,3],[22,4,22,6],[22,8,22,10],[22,11,22,12]]}
["Steam Boiler (PAGE 1)",null,null,null,null,null,"BUILDING NAME____________________________________",null,null,"MONTH________________________",null,"YEAR________"]
[null,"ANNUAL TASKS/SUMMER OVERHAUL",null,null,null,null,"LOCATION _______________________________",null,null,"OPERATOR NAME_______________________"]
[null,"*This task may require special service training",null,null,null,null,"EQUIPMENT ID ____________________________",null,null,"EMERGENCY CONTACT___________________"]
[null,"PROCEDURE",null,null,"TASK DETAILS/EXPLANATION",null,null,"COMPLETE?","COMMENTS / ISSUES",null,null,"SIGN"]
[null,"TESTING SAFETIES AND EFFICIENCY"]
[1,"Clean low-water cut-offs",null,null,"Thoroughly clean the low water cut-offs.  Open them up to remove built up sediment, ensure the float is not water-logged.  Replace gasket if needed."]
[2,"Test the pressure relief valves",null,null,"The relief valve should vent water when the test lever is lifted. It should not weep or discharge water at normal system pressure."]
[3,"Clean and adjust burner components*",null,null,"Inspect burner components; diffuser, nozzle, IR/UV scanner, electrode, etc.  Clean if dirty.  Replace if broken.  "]
[4,"Test boiler efficiency*",null,null,"Use a combustion analyzer to ensure that the burner is adjusted properly.  Attach the printout to this form or write the results in the comment box to the right.  This must be done any time a change is made which affects the fuel or air ratio entering the burner."]
[null,"CLEANING/TUNING"]
[1,"Clean the fireside of the boiler (Oil Only)*",null,null,"If the flue temperature exceeds 550°F, the boiler needs to be cleaned"]
[2,"Clean waterside of the boiler*",null,null,"Drain the boiler and inspect the waterside through access ports.  Use a droplight to inspect for scale build-up.  Use a pressure washer to remove scale.  Thoroughly flush out through the blow-downs or bottom ports."]
[3,"Inspect the refractory walls of the combustion chamber",null,null,"Visually inspect the combustion chamber, make sure all the refractory bricks are in the correct place and the boiler is completely sealed.  If there are signed of flame damage on the boiler jacket, there may be cracks in the refractory.  Find the cracks and repair with fiberglass rope and furnace cement."]
[4,"Clean the exhaust flue",null,null,"Thoroughly inspect the exhaust flue for any signs of\nblockage, corrosion or leakage."]
[5,"Conduct a bottom-blowdown of the boiler*",null,null,"For best results isolate the boiler from the heating system by closing the \"king valve\", build up 5-10 psi of pressure, then open the bottom blow-down to clear out the sediment in the mud-drums."]
[6,"Confirm proper flame*",null,null,"Observe the flame during combustion, ensure it has the correct color and shape and is not making contact with the refractory walls of the boiler."]
["Steam Boiler (PAGE 2)",null,null,null,null,null,"BUILDING NAME____________________________________",null,null,"MONTH________________________",null,"YEAR________"]
[null,"ANNUAL TASKS/SUMMER OVERHAUL",null,null,null,null,"LOCATION _______________________________",null,null,"OPERATOR NAME_______________________"]
[null,"*This task may require special service training",null,null,null,null,"EQUIPMENT ID ____________________________",null,null,"EMERGENCY CONTACT___________________"]
[null,"PROCEDURE",null,null,"TASK DETAILS/EXPLANATION",null,null,"COMPLETE?","COMMENTS / ISSUES",null,null,"SIGN"]
[null,"CLEANING/TUNING (continued)"]
[7,"Ensure proper pressuretrol settings*",null,null,"Observe the boiler through at least one complete cycle.  Make note of what pressure the boiler turns ON and what pressure the boiler turns OFF.  Wright the time of the cycle in the comment box to the right.  Make sure the operating pressure set pt is no more than 5 psi and make sure the modulating pressure setting is below the operating pressure set point"]
[8,"Ensure efficiency controls are working properly",null,null,"Observe the boiler through at least one complete cycle.  Make note of the outside temperature and how long the cycle lasts.  Record how long between two boiler cycles."]
[9,"Clean oil filters (Oil Only)",null,null,"If burning oil, clean or replace the fuel oil filters."]

{"sheet":"C-SteamBoiler_Monthly","index":25,"n_rows":16,"n_cols":12,"rows_kept":16,"cut":false,"hidden":true,"merged":[[3,1,3,3],[3,4,3,6],[3,8,3,10],[3,11,3,12],[4,11,4,12],[8,11,8,12],[9,1,9,3],[9,4,9,6],[9,8,9,10],[5,1,5,3],[5,4,5,6],[5,8,5,10],[5,11,5,12],[6,1,6,3],[6,4,6,6],[6,8,6,10],[6,11,6,12],[7,1,7,3],[7,4,7,6],[7,8,7,10],[7,11,7,12],[9,11,9,12],[11,1,11,3],[11,4,11,6],[11,8,11,10],[11,11,11,12],[10,1,10,3],[10,4,10,6],[10,8,10,10],[10,11,10,12],[12,1,12,3],[12,4,12,6],[12,8,12,10],[12,11,12,12],[15,1,15,3],[15,4,15,6],[15,8,15,10],[15,11,15,12],[13,1,13,3],[13,4,13,6],[13,8,13,10],[13,11,13,12],[14,1,14,3],[14,4,14,6],[14,8,14,10],[14,11,14,12]]}
["Steam Boiler ",null,null,null,null,null,"BUILDING NAME____________________________________",null,null,"MONTH________________________",null,"YEAR__________"]
[null,"MONTHLY TASKS",null,null,null,null,"LOCATION _______________________________",null,null,"OPERATOR NAME________________"]
[null,"*This task may require special service training",null,null,null,null,"EQUIPMENT ID ____________________________",null,null,"EMERGENCY CONTACT____________"]
["#","PROCEDURE",null,null,"TASK DETAILS/EXPLANATION",null,null,"COMPLETE?","COMMENTS / ISSUES",null,null,"SIGN"]
[null,"TESTING SAFETIES AND EFFICIENCY"]
[1,"Test low-water cut-offs",null,null,"Ensure that the low water cutoff device(s) function(s) properly. Test in accordance with the manufacturer’s instructions included with the device(s)."]
[2,"Test the pressure relief valves",null,null,"The relief valve should vent water when the test lever is lifted. It should not weep or discharge water at normal system pressure."]
[3,"Conduct a boiler efficiency test*",null,null,"Use a combustion analyzer to ensure that the burner is adjusted properly.  Attach the printout to this form or write the results in the comment box to the right.  This must be done anytime a change is made which affects the fuel or air ratio entering the burner."]
[null,"CLEANING/TUNING"]
[1,"Clean the fireside of the boiler (Oil Only)*",null,null,"If the flue temperature exceeds 550°F, the boiler needs to be cleaned."]
[2,"Clean the exhaust flue",null,null,"Thoroughly inspect the exhaust flue for any signs of blockage, corrosion or leakage."]
[3,"Conduct a bottom-blowdown of the boiler*",null,null,"Open the bottom blow-down valve to clear out the sediment in the mud-drums.  Close the valve once the exiting water appears clear. "]
[4,"Confirm proper flame*",null,null,"Observe the flame during combustion, ensure it has the correct color and shape and is not making contact with the refractory walls of the boiler."]
[5,"Ensure proper pressuretrol settings*",null,null,"Observe the boiler through at least one complete cycle.  Make note of what pressure the boiler turns ON and what pressure the boiler turns OFF.  Wright the time of the cycle in the comment box to the right.  Make sure the operating pressure set pt is no more than 5 psi and make sure the modulating pressure setting is below the operating pressure set point"]
[6,"Ensure efficiency controls are working properly",null,null,"Observe the boiler through at least one complete cycle.  Make note of the outside temperature and how long the cycle lasts.  Record how long between two boiler cycles."]
[7,"Clean oil filters (Oil Only)",null,null,"If burning oil, clean or replace the fuel oil filters."]

{"sheet":"C-SteamBoiler_Daily","index":26,"n_rows":36,"n_cols":24,"rows_kept":36,"cut":false,"hidden":true,"merged":[[5,13,5,14],[5,15,5,16],[3,13,3,14],[3,15,3,16],[4,0,4,2],[4,13,4,14],[4,15,4,16],[6,13,6,14],[6,15,6,16],[7,13,7,14],[7,15,7,16],[8,13,8,14],[8,15,8,16],[9,13,9,14],[9,15,9,16],[10,13,10,14],[10,15,10,16],[11,13,11,14],[11,15,11,16],[12,13,12,14],[12,15,12,16],[13,13,13,14],[13,15,13,16],[14,13,14,14],[14,15,14,16],[15,13,15,14],[15,15,15,16],[16,13,16,14],[16,15,16,16],[17,13,17,14],[17,15,17,16],[18,13,18,14],[18,15,18,16],[19,13,19,14],[19,15,19,16],[20,13,20,14],[20,15,20,16],[21,13,21,14],[21,15,21,16],[22,13,22,14],[22,15,22,16],[23,13,23,14],[23,15,23,16],[24,13,24,14],[24,15,24,16],[25,13,25,14],[25,15,25,16],[26,13,26,14],[26,15,26,16],[27,13,27,14],[27,15,27,16],[28,13,28,14],[28,15,28,16],[29,13,29,14],[29,15,29,16],[30,13,30,14],[30,15,30,16],[31,13,31,14],[31,15,31,16],[32,13,32,14],[32,15,32,16],[33,13,33,14],[33,15,33,16],[34,13,34,14],[34,15,34,16],[35,13,35,14],[35,15,35,16]]}
[null,"Steam Boiler ",null,null,null,null,"BUILDING______________________",null,null,null,null,"MONTH________________________",null,"YEAR______",null,null,null,"Steam Boiler ",null,null,null,"MONTH________________________",null,"YEAR________"]
[null,"DAILY INSPECTION",null,null,null,null,"LOCATION_________________________",null,null,null,null,"OPERATOR NAME___________________________",null,null,null,null,null,{"$f":"B2","v":"DAILY INSPECTION"},null,null,null,"OPERATOR NAME___________________"]
[null,null,null,null,null,null,"EQUIPMENT ID__________________",null,null,null,null,"EMERGENCY CONTACT_______________________",null,null,null,null,null,null,null,null,null,"EMERGENCY CONTACT_______________"]
["DAY","TIME","Outside Air Temp (°F)","Burner Control Set on AUTO?","Burner Runtime (hours)","Operating Pressure-trol Setting (psi)","Operating Pressure (psi)","Boiler Water Level","Highest Stack Temp (°F)","Condensate Tank Temp (°F)","Check Condensate Tank for Leaks","Make-up Water Reading (gal.)","Gas Meter Reading","COMMENTS /  ISSUES",null,"SIGN",null,"Additional COMMENTS/ISSUES"]
["Call Manager \nIF:",null,null,"NO","large change in daily hours","above 5 psi","above 5 psi","too high or too low","above 500","above 200","leaks present","large change in daily amount","large change in daily amount","if comments made"]
[1,null,null,"Y       N"]
[2,null,null,"Y       N"]
[3,null,null,"Y       N"]
[4,null,null,"Y       N"]
[5,null,null,"Y       N"]
[6,null,null,"Y       N"]
[7,null,null,"Y       N"]
[8,null,null,"Y       N"]
[9,null,null,"Y       N"]
[10,null,null,"Y       N"]
[11,null,null,"Y       N"]
[12,null,null,"Y       N"]
[13,null,null,"Y       N"]
[14,null,null,"Y       N"]
[15,null,null,"Y       N"]
[16,null,null,"Y       N"]
[17,null,null,"Y       N"]
[18,null,null,"Y       N"]
[19,null,null,"Y       N"]
[20,null,null,"Y       N"]
[21,null,null,"Y       N"]
[22,null,null,"Y       N"]
[23,null,null,"Y       N"]
[24,null,null,"Y       N"]
[25,null,null,"Y       N"]
[26,null,null,"Y       N"]
[27,null,null,"Y       N"]
[28,null,null,"Y       N"]
[29,null,null,"Y       N"]
[30,null,null,"Y       N"]
[31,null,null,"Y       N"]

{"sheet":"C-CoolingTower_Annual","index":27,"n_rows":15,"n_cols":12,"rows_kept":15,"cut":false,"hidden":true,"merged":[[13,1,13,3],[13,4,13,6],[13,8,13,10],[13,11,13,12],[14,1,14,3],[14,4,14,6],[14,8,14,10],[14,11,14,12],[11,1,11,3],[11,4,11,6],[11,8,11,10],[11,11,11,12],[12,1,12,3],[12,4,12,6],[12,8,12,10],[12,11,12,12],[9,1,9,3],[9,4,9,6],[9,8,9,10],[9,11,9,12],[10,1,10,3],[10,4,10,6],[10,8,10,10],[10,11,10,12],[7,1,7,3],[7,4,7,6],[7,8,7,10],[7,11,7,12],[8,1,8,3],[8,4,8,6],[8,8,8,10],[8,11,8,12],[6,1,6,3],[6,4,6,6],[6,8,6,10],[6,11,6,12],[4,1,4,3],[4,4,4,6],[4,8,4,10],[4,11,4,12],[5,11,5,12]]}
["COOLING TOWER",null,null,null,null,"BUILDING NAME____________________________________",null,null,null,"MONTH_____________________________",null,"YEAR_____"]
[null,"ANNUAL TASKS",null,null,null,"LOCATION _______________________________________",null,null,null,"OPERATOR NAME__________________________"]
[null,"At the end of the cooling season.",null,null,null,"EQUIPMENT ID ______________________________________",null,null,null,"EMERGENCY CONTACT_____________________"]
[]
[null,"PROCEDURE",null,null,"TASK DETAILS/EXPLANATION",null,null,"COMPLETE?","COMMENTS / ISSUES",null,null,"SIGN"]
[]
[1,"Drain evaporative cooling unit.",null,null,"The cold water basin should be drained completely.  Leave basin drain open."]
[2,"Clean cold water basin.",null,null,"The cold water basin should be flushed and cleaned with the suction strainer screens in place."]
[3,"Clean suction strainer screens.",null,null,"Clean then re-install the suction strainer screens"]
[4,"Lubricate fan shaft bearings and motor base adjusting screws.",null,null,"This should also be performed if the unit is going to sit idle prior to start-up."]
[5,"Drain make-up water line and close valve.",null,null,"All water make-up, overflow and drain piping needs to be drained, if not heat traced and insulated."]
[6,"Inspect and clean the finish of the unit",null,null,"Clean and refinish as required"]
[7,"Check condition of belt.",null,null,"Inspect the fan belts for cracks, signs of fraying.  Replace if needed."]
[8,"Inspect/Clean blockages in fill material and air inlet louvers."]
[9]

{"sheet":"C-CoolingTower_Daily","index":28,"n_rows":36,"n_cols":19,"rows_kept":36,"cut":false,"hidden":true,"merged":[[33,8,33,9],[33,10,33,11],[34,8,34,9],[34,10,34,11],[35,8,35,9],[35,10,35,11],[30,8,30,9],[30,10,30,11],[31,8,31,9],[31,10,31,11],[32,8,32,9],[32,10,32,11],[27,8,27,9],[27,10,27,11],[28,8,28,9],[28,10,28,11],[29,8,29,9],[29,10,29,11],[24,8,24,9],[24,10,24,11],[25,8,25,9],[25,10,25,11],[26,8,26,9],[26,10,26,11],[21,8,21,9],[21,10,21,11],[22,8,22,9],[22,10,22,11],[23,8,23,9],[23,10,23,11],[18,8,18,9],[18,10,18,11],[19,8,19,9],[19,10,19,11],[20,8,20,9],[20,10,20,11],[15,8,15,9],[15,10,15,11],[16,8,16,9],[16,10,16,11],[17,8,17,9],[17,10,17,11],[12,8,12,9],[12,10,12,11],[13,8,13,9],[13,10,13,11],[14,8,14,9],[14,10,14,11],[9,8,9,9],[9,10,9,11],[10,8,10,9],[10,10,10,11],[11,8,11,9],[11,10,11,11],[6,8,6,9],[6,10,6,11],[7,8,7,9],[7,10,7,11],[8,8,8,9],[8,10,8,11],[5,8,5,9],[5,10,5,11],[3,8,3,9],[3,10,3,11],[4,0,4,2],[4,8,4,9],[4,10,4,11]]}
[null,"COOLING TOWER",null,null,null,"BUILDING NAME _____________________________",null,null,null,"MONTH __________________________","Year_____",null,"COOLING TOWER","BUILDING NAME____________________________________",null,null,"MONTH________________________",null,"YEAR________"]
[null,"DAILY INSPECTION",null,null,null,"LOCATION _______________________________________",null,null,null,"OPERATOR NAME __________________________",null,null,{"$f":"B2","v":"DAILY INSPECTION"},"Energy Mgmt Contact ____________________________________",null,null,"OPERATOR NAME__________________________"]
[null,null,null,null,null,"EQUIPMENT ID ______________________________________",null,null,null,"EMERGENCY CONTACT _________________________",null,null,null,null,null,null,"EMERGENCY CONTACT______________________"]
["DAY","TIME","Outside Air Temp (°F)","Check unit for debris / blockages","Listen for unusual noise or vibration","Check Operation of Fans","Check Water Basin Level","Make-up Water Reading (gal.)","COMMENTS / ISSUES",null,"SIGN / INITIAL",null,"Additional COMMENTS/ISSUES"]
["Call Manager IF:",null,null,"debris found","unusual noise","not working","too high or too low","large change in daily amount","if comments made"]
[1]
[2]
[3]
[4]
[5]
[6]
[7]
[8]
[9]
[10]
[11]
[12]
[13]
[14]
[15]
[16]
[17]
[18]
[19]
[20]
[21]
[22]
[23]
[24]
[25]
[26]
[27]
[28]
[29]
[30]
[31]

{"sheet":"C-Chiller_Daily","index":29,"n_rows":36,"n_cols":24,"rows_kept":36,"cut":false,"hidden":true,"merged":[[35,13,35,14],[35,15,35,16],[32,13,32,14],[32,15,32,16],[33,13,33,14],[33,15,33,16],[34,13,34,14],[34,15,34,16],[29,13,29,14],[29,15,29,16],[30,13,30,14],[30,15,30,16],[31,13,31,14],[31,15,31,16],[26,13,26,14],[26,15,26,16],[27,13,27,14],[27,15,27,16],[28,13,28,14],[28,15,28,16],[23,13,23,14],[23,15,23,16],[24,13,24,14],[24,15,24,16],[25,13,25,14],[25,15,25,16],[20,13,20,14],[20,15,20,16],[21,13,21,14],[21,15,21,16],[22,13,22,14],[22,15,22,16],[17,13,17,14],[17,15,17,16],[18,13,18,14],[18,15,18,16],[19,13,19,14],[19,15,19,16],[14,13,14,14],[14,15,14,16],[15,13,15,14],[15,15,15,16],[16,13,16,14],[16,15,16,16],[11,13,11,14],[11,15,11,16],[12,13,12,14],[12,15,12,16],[13,13,13,14],[13,15,13,16],[8,13,8,14],[8,15,8,16],[9,13,9,14],[9,15,9,16],[10,13,10,14],[10,15,10,16],[5,13,5,14],[5,15,5,16],[6,13,6,14],[6,15,6,16],[7,13,7,14],[7,15,7,16],[3,13,3,14],[3,15,3,16],[4,0,4,3],[4,8,4,11],[4,13,4,14],[4,15,4,16]]}
[null,"CHILLER",null,null,null,"BUILDING NAME____________________________________",null,null,null,null,null,null,"MONTH_____________________________",null,null,"YEAR_____",null,"CHILLER","BUILDING NAME____________________________________",null,null,"MONTH________________________",null,"YEAR________"]
[null,"DAILY INSPECTION",null,null,null,"LOCATION __________________________________________",null,null,null,null,null,null,"OPERATOR NAME__________________________",null,null,null,null,{"$f":"B2","v":"DAILY INSPECTION"},"Energy Mgmt Contact ____________________________________",null,null,"OPERATOR NAME__________________________"]
[null,null,null,null,null,"EQUIPMENT ID ______________________________________",null,null,null,null,null,null,"EMERGENCY CONTACT_____________________",null,null,null,null,null,null,null,null,"EMERGENCY CONTACT______________________"]
["DAY","TIME","Outside Air Temp (°F)","Relative Humidity (% RH)"," Runtime (hours)","% Load","Evap. CHW Supply Temp (°F)","Evap. CHW Return Temp (°F)","CHW Supply Press (psi)","Cond. Entering Temp (°F)","Cond. Leaving Temp (°F)","Cooling Tower Supply Press (psi)","Check Pumps for Noise / Leaks","COMMENTS / ISSUES",null,"SIGN / INITIAL",null,"Additional COMMENTS/ISSUES"]
["Call Manager IF:",null,null,null,"large change in daily hours","100% when OAT < 90","> 45 when OAT > 90","> 55 when OAT > 90","depends on system",null,null,null,"leaks present","if comments made"]
[1]
[2]
[3]
[4]
[5]
[6]
[7]
[8]
[9]
[10]
[11]
[12]
[13]
[14]
[15]
[16]
[17]
[18]
[19]
[20]
[21]
[22]
[23]
[24]
[25]
[26]
[27]
[28]
[29]
[30]
[31]

{"sheet":"C-RTU_Annual","index":30,"n_rows":16,"n_cols":12,"rows_kept":16,"cut":false,"hidden":true,"merged":[[3,1,3,3],[3,4,3,6],[3,8,3,10],[3,11,3,12],[4,0,4,12],[8,1,8,3],[8,4,8,6],[8,8,8,10],[8,11,8,12],[5,1,5,3],[5,4,5,6],[5,8,5,10],[5,11,5,12],[6,1,6,3],[6,4,6,6],[6,8,6,10],[6,11,6,12],[7,1,7,3],[7,4,7,6],[7,8,7,10],[7,11,7,12],[9,0,9,12],[11,1,11,3],[11,4,11,6],[11,8,11,10],[11,11,11,12],[10,1,10,3],[10,4,10,6],[10,8,10,10],[10,11,10,12],[12,1,12,3],[12,4,12,6],[12,8,12,10],[12,11,12,12],[15,1,15,3],[15,4,15,6],[15,8,15,10],[15,11,15,12],[13,1,13,3],[13,4,13,6],[13,8,13,10],[13,11,13,12],[14,1,14,3],[14,4,14,6],[14,8,14,10],[14,11,14,12]]}
["RTU/AHU",null,null,"**ENSURE UNIT POWER IS OFF BEFORE SERVICE**",null,null,"BUILDING NAME______________________",null,"MONTH ________________",null,null,"YEAR _______"]
[null,"ANNUAL TASKS",null,null,null,null,"LOCATION __________________________","OPERATOR NAME ___________________"]
[null,"*This task may require special service training",null,null,null,null,"EQUIPMENT ID _______________________","EMERGENCY CONTACT _______________"]
[null,"PROCEDURE",null,null,"TASK DETAILS/EXPLANATION",null,null,"COMPLETE?","COMMENTS",null,null,"SIGN"]
["COOLING EQUIPMENT"]
[1,"Clean the evaporator and condenser coils*",null,null,"Follow instructions as closely as possible to avoid damage to coils:\n1. Remove all surface debris and dirt with a vacuum cleaner. (Use of a water stream, such as a garden hose, against a surface-loaded coil will drive the fibers and dirt into the coil and make it harder to clean.  Surface debris must be completely removed before using low-velocity clean water rinse.)\n2. Spray both sides of coil with the cleaning solution until completely saturated.\n3. Rinse throughly with clean water to remove residual cleaning agent and contamination.\n4. Flush the condensate pan after completion. "]
[2,"Check air damper movement",null,null,"Inspect all air damper hinges and pins to ensure that all moving parts are securely mounted. Keep the blades clean as necessary. Verify that all damper linkages move freely; lubricate with white grease, if necessary."]
[3,"Check/clean ALL fans and motors",null,null,"Check fan motor bearings; repair or replace the motor as necessary. Check the fan shaft bearings for wear. Replace the bearings as necessary.  Clean dirt from leading edge of fan blades."]
[4,"Confirm proper refrigerant levels and performance*",null,null,"With the unit running, check and record the: ambient temperature; compressor suction and discharge pressures (each circuit); superheat (each circuit);  Record data in an “operator’s maintenance log”. If the operating pressures indicate a refrigerant shortage, measure the system superheat. For guidelines, refer to the “Compressor Start-Up” section in operating manual.  *Important: Do not release refrigerant to the atmosphere! If adding or removing refrigerant is required, the service technician must comply with all federal, state and local laws.*"]
["GAS-FIRED HEATING EQUIPMENT"]
[1,"Check for proper gas supply pressure*",null,null,"Gas line pressure entering the unit’s main gas valve must be within specified ranges. Adjust unit gas regulator valve as required."]
[2,"Flue gas passageway inspection",null,null," Inspect the flue collector box and upper areas of the heat exchanger. Remove the combustion blower wheel and motor assembly. Remove the flue cover to inspect the heat exchanger. Clean all surfaces as required using a wire brush."]
[3,"Inspect the BLOWERS ",null,null,"Check the blower wheel for debris and clean if necessary. The blower motors are prelubricated for extended bearing life. No further lubrication is needed."]
[4,"Inspect the main burners",null,null,"Inspect for deterioration or blockage due to corrosion or other causes. To access burners, remove burner access panel and slide out burner partition.Observe the main burner flames and adjust, if necessary."]
[5,"Clean and adjust the main burners",null,null,"1. Inspect burners; if dirty, remove burners from rack. (Mark each burner to identify its position before removing from rack.)\n2. Use a soft brush to clean burners and cross-over port as required.\n3. Adjust spark gap."]
[6,"Conduct a combustion analysis to ensure proper combustion*",null,null,"It is critical that the gas supplied to the unit be completely burned to avoid the production of carbon monoxide gas. Complete combustion of the gas requires, but is not limited to, correct gas pressure and gas flow rate, adequate combustion, air, and proper\nventing."]

{"sheet":"C-RTU_Monthly","index":31,"n_rows":16,"n_cols":12,"rows_kept":16,"cut":false,"hidden":true,"merged":[[5,1,5,3],[5,4,5,6],[5,8,5,10],[5,11,5,12],[3,1,3,3],[3,4,3,6],[3,8,3,10],[3,11,3,12],[4,11,4,12],[6,1,6,3],[6,4,6,6],[6,8,6,10],[6,11,6,12],[7,1,7,3],[7,4,7,6],[7,8,7,10],[7,11,7,12],[8,1,8,3],[8,4,8,6],[8,8,8,10],[8,11,8,12],[9,1,9,3],[9,4,9,6],[9,8,9,10],[9,11,9,12],[13,1,13,3],[13,4,13,6],[13,8,13,10],[13,11,13,12],[10,0,10,12],[11,1,11,3],[11,4,11,6],[11,8,11,10],[11,11,11,12],[12,1,12,3],[12,4,12,6],[12,8,12,10],[12,11,12,12]]}
["RTU/AHU",null,null,"**ENSURE UNIT POWER IS OFF BEFORE SERVICE**",null,null,"BUILDING NAME____________________________________",null,"MONTH ________________________",null,null,"YEAR _________"]
[null,"MONTHLY TASKS",null,null,null,null,"LOCATION ______________",null,"OPERATOR NAME ________________________"]
[null,"*This task may require special service training",null,null,null,null,"EQUIPMENT ID ______________",null,"EMERGENCY CONTACT _____________________"]
[null,"PROCEDURE",null,null,"TASK DETAILS/EXPLANATION",null,null,"COMPLETE?","COMMENTS / ISSUES",null,null,"SIGN"]
["COOLING EQUIPMENT"]
[1,"Condenser and evaporator coil cleanliness checked",null,null,"Inspect the evaporator and condenser coils for dirt, bent fins, etc. If the coils appear dirty, clean them according to the instructions described in RTU/AHU Annual Tasks"]
[2,"Condensate drain checked",null,null,"Check the unit’s drain pans and condensate piping to ensure that there are no blockages."]
[3,"Clean or replace ALL filters",null,null,"Inspect the unit’s air filters. If necessary, clean or replace them."]
[4,"Clean or replace outside inlet air filters",null,null,"If filters are permanent aluminum-mesh type filters, Clean by washing with hot low-pressure water and soft detergent and replace all screens before restarting the unit. Observe the flow direction arrows on the side of each filter frame."]
[5,"Check the condition and tension of ALL belts*",null,null,"Inspect the belt for signs of cracking, fraying or glazing along the inside surfaces. Check belt tension by using a spring--force tool (such as a Browning or Gates Belt Tension gauge or equivalent tool);  Replacement is necessary if the belts appear frayed or worn. Units with dual belts require a matched set of belts to ensure equal belt length. When removing or installing the new belts, do not stretch them over the sheaves. Loosen the belts using the belt tension adjustment bolts on the motor mounting base."]
["GAS-FIRED HEATING EQUIPMENT"]
[1,"Conduct a general visual inspection of the heating unit",null,null,"a. All flue product carrying areas external to the unit (i.e. chimney, vent connector) are clear and free of obstruction."]
[2,null,null,null,"b. The burner flames are in good adjustment without erratic flames. "]
[3,null,null,null,"c. Fresh air inlet and vent are not blocked and free from obstruction."]
["EQUIPMENT APPEARANCE",null,null,null,null,null,null,"Typical Indoor Air Handling Unit (AHU)"]
[null,"Typical Roof Top Unit (RTU)"]

{"sheet":"C-ForcedAirHeating_Annual","index":32,"n_rows":15,"n_cols":12,"rows_kept":15,"cut":false,"hidden":true,"merged":[[6,1,6,3],[6,4,6,6],[6,8,6,10],[6,11,6,12],[4,1,4,3],[4,4,4,6],[4,8,4,10],[4,11,4,12],[5,11,5,12],[7,1,7,3],[7,4,7,6],[7,8,7,10],[7,11,7,12],[8,1,8,3],[8,4,8,6],[8,8,8,10],[8,11,8,12],[9,1,9,3],[9,4,9,6],[9,8,9,10],[9,11,9,12],[10,1,10,3],[10,4,10,6],[10,8,10,10],[10,11,10,12],[11,1,11,3],[11,4,11,6],[11,8,11,10],[11,11,11,12],[12,1,12,3],[12,4,12,6],[12,8,12,10],[12,11,12,12],[13,1,13,3],[13,4,13,6],[13,8,13,10],[13,11,13,12],[14,1,14,3],[14,4,14,6],[14,8,14,10],[14,11,14,12]]}
["FORCED AIR HEATING UNIT",null,null,null,null,null,"BUILDING NAME____________________________________",null,"MONTH ________________",null,null,"YEAR _________"]
[null,"ANNUAL TASKS",null,null,null,null,"LOCATION ______________",null,"OPERATOR NAME ________________________"]
[null,"**ENSURE UNIT POWER IS OFF BEFORE SERVICE**",null,null,null,null,"EQUIPMENT ID ______________",null,"EMERGENCY CONTACT ____________________"]
[]
["#","PROCEDURE",null,null,"TASK DETAILS/EXPLANATION",null,null,"COMPLETE?","COMMENTS / ISSUES",null,null,"SIGN"]
["HEATING UNIT TASKS"]
[1,"Inspect the BLOWERS ",null,null,"Check the blower wheel for debris and clean if necessary. The blower motors are prelubricated for extended bearing life. No further lubrication is needed."]
[2,"Clean and adjust the main burners (Gas Only)",null,null,"1. Inspect burners; if dirty, remove burners from rack. (Mark each burner to identify its position before removing from rack.)\n2. Use a soft brush to clean burners and cross-over port as required.\n3. Adjust spark gap."]
[3,"Inspect HEAT EXCHANGER (Gas Only)",null,null,"These items must be inspected for signs of corrosion, and/ or deterioration at the beginning of each heating season by a qualified service technician and cleaned annually for best operation."]
[4,"Check room for caustic vapor products.",null,null,"the warm air furnace should NOT be operated in a corrosive atmosphere. Paint solvents, cleaning chemicals, spray propellants, chlorine, flourine and bleaches should not be used in the vicinity of the furnace during normal operation."]
[5,"Inspect exterior exhaust flue pipes (Gas Only)",null,null,"Must be inspected for signs of water, damaged or sagging pipe, or disconnected joints. After any heavy snow, ice or frozen fog event, the furnace vent pipes may become restricted. Always check the vent system and remove any snow or ice that may be obstructing the intake or exhaust pipes."]
[6,"Inspect the air intake to the unit",null,null,"Fresh air grilles and louvers (on the unit and in the room where the furnace is installed) − Must be open and unobstructed to provide combustion air.  DO NOT obstruct air flow to unit. Unit must receive an unobstructed flow of combustion and ventilating air. DO NOT block or obstruct air openings on the furnace or air openings to the area in which the furnace is installed."]
[7,"Inspect blower access door",null,null,"Must be properly in place and provide a seal between the return air and the room where the furnace is installed."]
[8,"Conduct a combustion analysis to ensure proper combustion (Gas Only)*",null,null,"It is critical that the gas supplied to the unit be completely burned to avoid the production of carbon monoxide gas. Complete combustion of the gas requires, but is not limited to, correct gas pressure and gas flow rate, adequate combustion, air, and proper venting."]
[9,"Check ductwork and air diffusors",null,null,"Ensure all ductwork is sealed tightly at all connection points.   Ensure the supply air diffusors and return vents are clean of dust and debris.  Remove the covers and ensure the ductwork is sealed against the dry wall."]

{"sheet":"C-ForcedAirHeating_Monthly","index":33,"n_rows":14,"n_cols":12,"rows_kept":14,"cut":false,"hidden":true,"merged":[[5,1,5,3],[5,4,5,6],[5,8,5,10],[5,11,5,12],[3,1,3,3],[3,4,3,6],[3,8,3,10],[3,11,3,12],[4,11,4,12],[8,0,8,12],[9,1,9,3],[9,4,9,6],[9,8,9,10],[9,11,9,12],[6,1,6,3],[6,4,6,6],[6,8,6,10],[6,11,6,12],[7,1,7,3],[7,4,7,6],[7,8,7,10],[7,11,7,12],[10,8,10,10],[13,1,13,3],[13,4,13,6],[13,8,13,10],[13,11,13,12],[11,1,11,3],[11,4,11,6],[11,8,11,10],[11,11,11,12],[12,1,12,3],[12,4,12,6],[12,8,12,10],[12,11,12,12],[10,11,10,12],[10,1,10,3],[10,4,10,6]]}
["FORCED AIR HEATING UNIT",null,null,null,null,null,"BUILDING NAME____________________________________",null,null,"MONTH ________________",null,"YEAR ___________"]
[null,"MONTHLY TASKS",null,null,null,null,"LOCATION __________________",null,null,"OPERATOR NAME _____________________"]
[null,"**ENSURE UNIT POWER IS OFF BEFORE SERVICE**",null,null,null,null,"EQUIPMENT ID ______________",null,null,"EMERGENCY CONTACT _________________"]
[null,"PROCEDURE",null,null,"TASK DETAILS/EXPLANATION",null,null,"COMPLETE?","COMMENTS / ISSUES",null,null,"SIGN"]
["GENERAL TASKS"]
[1,"Clean or replace air filter",null,null,"If you have a semi-permanent filter, take the filter out of the frame and vacuum it. Where disposable filters are used, they must be replaced every month with the same size as originally supplied.  Air filters may also be located outside of the furnace using a remote filter grille. The filter grille could be in a hallway, wall, or in the ceiling."]
[2,"Set the temperature control",null,null,"Ensure programmable thermostat is setup for correct occupancy schedule and temperature."]
[3,"Check the condition of ALL belts",null,null,"Inspect the belt for signs of cracking, fraying or glazing along the inside surfaces. Replace if the belts are broken or appear frayed or worn."]
["GAS-FIRED HEATING EQUIPMENT"]
[1,"Conduct a general visual inspection of the heating unit",null,null,"a. All flue product carrying areas external to the unit (i.e. chimney, vent connector) are clear and free of obstruction."]
[2,null,null,null,"b. The vent connector is in place, slopes upward and is physically sound without holes or excessive corrosion."]
[3,null,null,null,"c. The return air duct connection(s) is physically sound, is sealed to the unit and terminates outside the space containing the unit."]
[4,null,null,null,"d. The burner flames are in good adjustment without erratic flames. "]
[5,null,null,null,"e. Fresh air inlet and vent are not blocked and free from obstruction. The horizontal or vertical vent and inlet must be located at least 12 inches minimum  above the normally expected snow accumulation level."]

{"sheet":"C-ForcedAirCooling_Annual","index":34,"n_rows":12,"n_cols":12,"rows_kept":12,"cut":false,"hidden":true,"merged":[[6,1,6,3],[6,4,6,6],[6,8,6,10],[6,11,6,12],[4,1,4,3],[4,4,4,6],[4,8,4,10],[4,11,4,12],[5,11,5,12],[7,1,7,3],[7,4,7,6],[7,8,7,10],[7,11,7,12],[8,1,8,3],[8,4,8,6],[8,8,8,10],[8,11,8,12],[11,1,11,3],[11,4,11,6],[11,8,11,10],[11,11,11,12],[9,1,9,3],[9,4,9,6],[9,8,9,10],[9,11,9,12],[10,1,10,3],[10,4,10,6],[10,8,10,10],[10,11,10,12]]}
["FORCED AIR COOLING UNIT",null,null,null,null,null,"BUILDING NAME____________________________________",null,"MONTH ________________",null,null,"YEAR _________"]
[null,"ANNUAL TASKS",null,null,null,null,"LOCATION ______________",null,"OPERATOR NAME __________________________"]
[null,"**ENSURE UNIT POWER IS OFF BEFORE SERVICE**",null,null,null,null,"EQUIPMENT ID ______________",null,"EMERGENCY CONTACT _________________________"]
[null,"*This task may require special service training"]
["#","PROCEDURE",null,null,"TASK DETAILS/EXPLANATION",null,null,"COMPLETE?","COMMENTS / ISSUES",null,null,"SIGN"]
["COOLING UNIT TASKS"]
[1,"Clean air filters",null,null,"Clean with a mild detergent in warm water, allow to dry throughly before reinstalling."]
[2,"Check thermostat",null,null,"Ensure programmable thermostat is setup for correct occupancy schedule and temperature."]
[3,"Clean indoor coil and outdoor coils and base pan*",null,null,"Use a biodigradable cleaning agent and degreaser.  **Do not use caustic coil cleaning agents or damage to alluminum fins or coil end plates may occur.** Use a soft brush and compressed air or vacuum.  A pressure washer may be used but take care not to bend the alluminum fins, use a sweeping motion in the same direction in alignment with the fins. This may require temporarily removing the unit."]
[4,"Inspect the BLOWERS ",null,null,"Check the blower wheel for debris and clean if necessary. The blower motors are prelubricated for extended bearing life. No further lubrication is needed."]
[5,"Inspect the air intake to the unit",null,null,"Fresh air grilles and louvers (on the unit and in the room\nwhere the unit is installed) − Must be open and unobstructed. Unit must receive an unobstructed flow of combustion and ventilating air. DO NOT block or obstruct air openings on the furnace or air openings to the area in which the unit is installed."]
[6,"Check ductwork and air diffusors",null,null,"Ensure all ductwork is sealed tightly at all connection points.   Ensure the supply air diffusors and return vents are clean of dust and debris.  Remove the covers and ensure the ductwork is sealed against the dry wall."]

{"sheet":"C-ForcedAirCooling_Monthly","index":35,"n_rows":15,"n_cols":12,"rows_kept":15,"cut":false,"hidden":true,"merged":[[5,1,5,3],[5,4,5,6],[5,8,5,10],[5,11,5,12],[3,1,3,3],[3,4,3,6],[3,8,3,10],[3,11,3,12],[4,11,4,12],[10,0,10,12],[6,1,6,3],[6,4,6,6],[6,8,6,10],[6,11,6,12],[7,1,7,3],[7,4,7,6],[7,8,7,10],[7,11,7,12],[8,0,8,12],[9,1,9,3],[9,4,9,6],[9,8,9,10],[9,11,9,12],[11,1,11,3],[11,4,11,6],[11,8,11,10],[11,11,11,12],[12,1,12,3],[12,4,12,6],[12,8,12,10],[12,11,12,12],[13,1,13,3],[13,4,13,6],[13,8,13,10],[13,11,13,12],[14,1,14,3],[14,4,14,6],[14,8,14,10],[14,11,14,12]]}
["FORCED AIR COOLING UNIT",null,null,null,null,null,"BUILDING NAME____________________________________",null,null,"MONTH ________________",null,"YEAR ___________"]
[null,"MONTHLY TASKS",null,null,null,null,"LOCATION ______________",null,null,"OPERATOR NAME _____________________"]
[null,"**ENSURE UNIT POWER IS OFF BEFORE SERVICE**",null,null,null,null,"EQUIPMENT ID ______________",null,null,"EMERGENCY CONTACT _________________"]
[null,"PROCEDURE",null,null,"TASK DETAILS/EXPLANATION",null,null,"COMPLETE?","COMMENTS / ISSUES",null,null,"SIGN"]
["GENERAL TASKS"]
[1,"Clean or replace air filter",null,null,"If you have a semi-permanent filter, take the filter out of the frame and vacuum it. Where disposable filters are used, they must be replaced every month with the same size as originally supplied.  Air filters may also be located outside of the furnace using a remote filter grille. The filter grille could be in a hallway, wall, or in the ceiling."]
[2,"Set the temperature control",null,null,"Ensure programmable thermostat is setup for correct occupancy schedule and temperature."]
[3,"Check the condition of ALL belts",null,null,"Inspect the belt for signs of cracking, fraying or glazing along the inside surfaces. Replace if the belts are broken or appear frayed or worn."]
["OUTDOOR COOLING EQUIPMENT"]
[1,"Check for blockages around outdoor heat pump unit",null,null,"Keep snow, ice and debris clear of the outdoor heat pump unit.  Efficient operation of your unit requires the free flow of air over the coils. Anything that blocks this flow forces the unit to work harder. At no time should anything be stacked against the side or draped over it."]
["INDOOR COOLING EQUIPMENT"]
[1,"Check drain pan",null,null,"Inspect the drain pad, ensure there are no blockages."]
[2,"Check for leaks",null,null,"Visually inspect the coils for areas of corrosion or possible leaks.  "]
[3,"Inspect the air intake to the unit",null,null,"Fresh air grilles and louvers (on the unit and in the room\nwhere the unit is installed) − Must be open and unobstructed. Unit must receive an unobstructed flow of combustion and ventilating air. DO NOT block or obstruct air openings on the furnace or air openings to the area in which the unit is installed."]
[4,"Listen for unusual noises",null,null,"Turn the unit on, allow unit to run through a couple cycles, listen for unusual noises."]

{"sheet":"C-DuctlessAC_Annual","index":36,"n_rows":17,"n_cols":12,"rows_kept":17,"cut":false,"hidden":true,"merged":[[3,1,3,3],[3,8,3,10],[3,11,3,12],[4,11,4,12],[5,1,5,3],[5,4,5,6],[5,8,5,10],[5,11,5,12],[6,1,6,3],[6,4,6,6],[6,8,6,10],[6,11,6,12],[7,1,7,3],[7,4,7,6],[7,8,7,10],[7,11,7,12],[8,1,8,3],[8,4,8,6],[8,8,8,10],[8,11,8,12],[9,1,9,3],[9,4,9,6],[9,8,9,10],[9,11,9,12],[10,1,10,3],[10,4,10,6],[10,8,10,10],[10,11,10,12],[11,1,11,3],[11,4,11,6],[11,8,11,10],[11,11,11,12],[13,1,13,3],[13,4,13,6],[13,8,13,10],[13,11,13,12],[14,1,14,3],[14,4,14,6],[14,8,14,10],[14,11,14,12]]}
["Ductless Mini-Split AC Unit Checklist",null,null,null,null,"BUILDING NAME____________________________________",null,null,null,"MONTH ________________",null,"YEAR _______"]
[null,"ANNUAL INSPECTION/TASKS",null,null,null,"LOCATION ______________",null,null,null,"OPERATOR NAME ________________"]
[null,"**ENSURE UNIT POWER IS OFF BEFORE SERVICE**",null,null,null,"EQUIPMENT ID ______________",null,null,null,"EMERGENCY CONTACT ____________"]
["#","PROCEDURE",null,null,"TASK DETAILS/EXPLANATION",null,null,"COMPLETE?","COMMENTS / ISSUES",null,null,"SIGN"]
["INDOOR UNIT TASKS"]
[1,"Clean air filters",null,null,"At the start of cooling season, every two weeks during season"]
[2,"Clean deodorizing filters (if applicable)",null,null,"At the start of cooling season"]
[3,"Clean anti-allergen filter (if applicable)",null,null,"At the start of cooling season"]
[4,"Ensure intake and outlet ports are not blocked",null,null,"At the start of cooling season"]
[5,"Clean the inside of the unit",null,null,"At the start of cooling season"]
[6,"Ensure programmable thermostat is setup for correct occupancy schedule",null,null,"At the start of cooling season"]
[7,"Decommission unit for the season",null,null,"At the end of cooling season"]
["OUTDOOR UNIT TASKS"]
[1,"Check the unit’s drain pans and condensate piping to ensure that there are no blockages, clean if needed.",null,null,"At the start of cooling season"]
[2,"Check air intake to ensure no air blockage from leaves or plastic bags",null,null,"At the start of cooling season, every two weeks during season"]
["EQUIPMENT APPEARANCE"]
[null,"Typical Indoor Unit",null,null,"Typical Outdoor Unit"]

{"sheet":"C-DuctlessAC_Monthly","index":37,"n_rows":12,"n_cols":12,"rows_kept":12,"cut":false,"hidden":true,"merged":[[3,1,3,3],[3,8,3,10],[3,11,3,12],[4,11,4,12],[5,1,5,3],[5,4,5,6],[5,8,5,10],[5,11,5,12],[9,1,9,3],[9,4,9,6],[9,8,9,10],[9,11,9,12],[6,1,6,3],[6,4,6,6],[6,8,6,10],[6,11,6,12],[8,1,8,3],[8,4,8,6],[8,8,8,10],[8,11,8,12]]}
["Ductless Mini-Split AC Unit Checklist",null,null,null,null,"BUILDING NAME____________________________________",null,null,null,"MONTH ________________",null,"YEAR _______"]
[null,"MONTHLY TASKS",null,null,null,"LOCATION ______________",null,null,null,"OPERATOR NAME ____________________"]
[null,"**ENSURE UNIT POWER IS OFF BEFORE SERVICE**",null,null,null,"EQUIPMENT ID ______________",null,null,null,"EMERGENCY CONTACT ________________"]
[null,"PROCEDURE",null,null,"TASK DETAILS",null,null,"COMPLETE?","COMMENTS / ISSUES",null,null,"SIGN"]
["INDOOR UNIT TASKS"]
[1,"Clean air filters",null,null,"At the start of cooling season, every month during season"]
[2,"Ensure programmable thermostat is setup for correct occupancy schedule."]
["OUTDOOR UNIT TASKS"]
[1,"Check the unit’s drain pans and condensate piping to ensure that there are no blockages, clean if needed."]
[2,"Check air intake to ensure no air blockage from leaves or plastic bags.",null,null,"At the start of cooling season, every month during season"]
["EQUIPMENT APPEARANCE"]
[null,"Typical Indoor Unit",null,null,"Typical Outdoor Unit"]

{"sheet":"C-PTAC_Annual","index":38,"n_rows":16,"n_cols":12,"rows_kept":16,"cut":false,"hidden":true,"merged":[[6,1,6,3],[6,4,6,6],[6,8,6,10],[6,11,6,12],[4,1,4,3],[4,4,4,6],[4,8,4,10],[4,11,4,12],[5,11,5,12],[7,1,7,3],[7,4,7,6],[7,8,7,10],[7,11,7,12],[8,1,8,3],[8,4,8,6],[8,8,8,10],[8,11,8,12],[9,1,9,3],[9,4,9,6],[9,8,9,10],[9,11,9,12],[10,1,10,3],[10,4,10,6],[10,8,10,10],[10,11,10,12],[13,1,13,3],[13,4,13,6],[13,8,13,10],[13,11,13,12],[11,1,11,3],[11,4,11,6],[11,8,11,10],[11,11,11,12],[12,1,12,3],[12,4,12,6],[12,8,12,10],[12,11,12,12]]}
["PTAC Checklist",null,null,null,null,null,"BUILDING NAME____________________________________",null,null,"MONTH ________________",null,"YEAR __________"]
[null,"ANNUAL INSPECTION/TASKS",null,null,null,null,"LOCATION ______________",null,null,"OPERATOR NAME _______________"]
[null,"**ENSURE UNIT POWER IS OFF BEFORE SERVICE**",null,null,null,null,"EQUIPMENT ID ______________",null,null,"EMERGENCY CONTACT____________"]
[null,"*This task may require special service training"]
["#","PROCEDURE",null,null,"TASK DETAILS/EXPLANATION",null,null,"COMPLETE?","COMMENTS / ISSUES",null,null,"SIGN"]
[null,"INDOOR UNIT TASKS"]
[1,"Clean air filters",null,null,"Clean with a mild detergent in warm water, allow to dry throughly before reinstalling."]
[2,"Check thermostat",null,null,"Ensure programmable thermostat is setup for correct occupancy schedule and temperature."]
[3,"Clean indoor coil and outdoor coils and base pan*",null,null,"Use a biodigradable cleaning agent and degreaser.  **Do not use caustic coil cleaning agents or damage to alluminum fins or coil end plates may occur.** Use a soft brush and compressed air or vacuum.  A pressure washer may be used but take care not to bend the alluminum fins, use a sweeping motion in the same direction in alignment with the fins. This may require temporarily removing the unit."]
[4,"Inspect inside the wall sleeve and drain system for dirt, clean if needed",null,null,"Clean with an antibacterial and antifungal cleaner.  Rinse both items throughly and ensure the drain outlets are operating correctly. "]
[5,"Check the seal around the sleeve and reseal as needed"]
[6,"Check for leaks",null,null,"Visually inspect the coils for areas of corrosion or possible leaks.  "]
[6,"Listen for unusual noises",null,null,"Turn the unit on, allow unit to run through a couple cycles, listen for unusual noises."]
[7]
["EQUIPMENT APPEARANCE"]
[null,"Typical Indoor Unit"]

{"sheet":"C-PTAC_Monthly","index":39,"n_rows":14,"n_cols":12,"rows_kept":14,"cut":false,"hidden":true,"merged":[[3,1,3,3],[3,8,3,10],[3,11,3,12],[4,11,4,12],[5,1,5,3],[5,4,5,6],[5,8,5,10],[5,11,5,12],[6,1,6,3],[6,4,6,6],[6,8,6,10],[6,11,6,12],[7,1,7,3],[7,4,7,6],[7,8,7,10],[7,11,7,12],[8,1,8,3],[8,4,8,6],[8,8,8,10],[8,11,8,12],[9,1,9,3],[9,4,9,6],[9,8,9,10],[9,11,9,12],[10,1,10,3],[10,4,10,6],[10,8,10,10],[10,11,10,12],[11,1,11,3],[11,4,11,6],[11,8,11,10],[11,11,11,12]]}
["PTAC Checklist",null,null,null,null,"BUILDING NAME____________________________________",null,null,null,"MONTH ________________",null,"YEAR ________"]
[null,"MONTHLY TASKS",null,null,null,"LOCATION ______________",null,null,null,"OPERATOR NAME _____________________"]
[null,"**ENSURE UNIT POWER IS OFF BEFORE SERVICE**",null,null,null,"EQUIPMENT ID ______________",null,null,null,"EMERGENCY CONTACT _________________"]
[null,"PROCEDURE",null,null,"TASK DETAILS/EXPLANATION",null,null,"COMPLETE?","COMMENTS / ISSUES",null,null,"SIGN"]
["INDOOR UNIT TASKS"]
[1,"Clean air filters",null,null,"With a mild detergent in warm water, allow to dry thoroughly before reinstalling."]
[2,"Check thermostat",null,null,"Ensure programmable thermostat is setup for correct occupancy schedule and temperature."]
[3,"Check drain pan",null,null,"Inspect the drain pad, ensure there are no blockages."]
[4,"Check the seal around the sleeve and reseal as needed"]
[5,"Check for leaks",null,null,"Visually inspect the coils for areas of corrosion or possible leaks.  "]
[6,"Listen for unusual noises",null,null,"Turn the unit on, allow unit to run through a couple cycles, listen for unusual noises."]
[7]
["EQUIPMENT APPEARANCE"]
[null,"Typical Indoor Unit"]

{"sheet":"R-SiteFeedback","index":40,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"R-Tools","index":41,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}